## Component_Data
Component ID | Level | Location | #Units/Length/Area | Component Name | Cost Unit | Comment
1 | Floor | Typical | 48 | Bolted shear tab gravity connections | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Shear Connections
6 | Story | 3 | 8 | Welded column splices, Column 150 plf < W < 300 plf | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Column Splices
86 | Floor | 5 | 4 | Post-Northridge RBS connection with welded web, beam one side of column only, beam depth <= W27 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | RBS Connection - One Sided with db<W27
87 | Floor | 2 | 4 | Post-Northridge RBS connection with welded web, beam one side of column only, beam depth >= W30 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | RBS Connection - One Sided with db>W30
87 | Floor | 3 | 4 | Post-Northridge RBS connection with welded web, beam one side of column only, beam depth >= W30 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | RBS Connection - One Sided with db>W30
87 | Floor | 4 | 4 | Post-Northridge RBS connection with welded web, beam one side of column only, beam depth >= W30 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | RBS Connection - One Sided with db>W30
88 | Floor | 5 | 4 | Post-Northridge RBS connection with welded web, beams both sides of column, beam depth <= W27 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | RBS Connection - Double Sided with db<W27
89 | Floor | 2 | 4 | Post-Northridge RBS connection with welded web, beams both sides of column, beam depth >= W30 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | RBS Connection - Double Sided with db>W30
89 | Floor | 3 | 4 | Post-Northridge RBS connection with welded web, beams both sides of column, beam depth >= W30 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | RBS Connection - Double Sided with db>W30
89 | Floor | 4 | 4 | Post-Northridge RBS connection with welded web, beams both sides of column, beam depth >= W30 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | RBS Connection - Double Sided with db>W30
417 | Floor | 1 | 4 | Hydraulic Elevator – Applies to most California Installations 1976 or later, most western states installations postdating 1982 and most U.S installations postdating 1998. | Costing per elevator. Elevator demand parameter shall be defined as the peak floor acceleration at the first floor. The elevator fragility for a multiple story building should only be entered once on the first floor. | Hydraulic Elevator - Situated on 1st Floor since its damage states are dependant on PGA
412 | Floor | Typical | 14000 | Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): A > 2500, Vert & Lat support | Costing for each 2500 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wire, diagonal wires, and compression posts, 2 inch wide ledger support angles at wall and oversize holes around tile openings. Includes lighting fixtures in suspended ceiling. | Suspended Ceiling - Floor foot print area > 2500 ft2 - 14000 ft2 is floor area since the repair cost is based on unit floor area (SF)
374 | Story | Typical | 600 | Wall Partition, Type: Gypsum + Wallpaper, Full Height, Fixed Below, Slip Track Above w/o returns (friction connection) | Costing based upon 9'x100' Panels | Drywall Partition - Length per floor is 600ft since the repair cost is based on unit 100 feet
324 | Story | Typical | 216 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes], 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | Costing is based on 1 unit | Exterior Glazing - Number of panes is 216 since the repair cost for this component is based on each pane (EP)
569 | Floor | Typical | 1536 | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - with designed bracing, SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, horizontal main and branches | Automatic Sprinklers - Length per floor is 1536 ft since the repair cost for this component is based on unit length (LF)
771 | Floor | Typical | 1400 | Corrugated slab (90mm steel; 100mm overlay) | Costing is based on a slab area of 10.764 square feet | Corrugated slab (90mm steel; 100mm overlay); 1400 ft2 represents the assumed affected slab area around columns 32columns * 4m2
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
Note on D1: Values must be specified in the same units of the project

## DATABASE
Database ID | Component Name | Number of Damage States | Controling EDP | Cost Unit Type/Value | Category | Component Short Name | Story
1 | Bolted shear tab gravity connections | 4 | SDR | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | Shear Connection | Floor
2 | Steel Column Base Plates, Column W < 150 plf | 4 | SDR | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | Column Base Plate
3 | Steel Column Base Plates, Column 150 plf < W < 300 plf | 4 | SDR | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | Column Base Plate
4 | Steel Column Base Plates, Column W > 300 plf | 4 | SDR | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | Column Base Plate
5 | Welded column splices, Column W < 150 plf | 3 | SDR | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | Column Splice
6 | Welded column splices, Column 150 plf < W < 300 plf | 3 | SDR | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | Column Splice
7 | Welded column splices, Column W > 300 plf | 3 | SDR | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | Column Splice
8 | Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace w < 40 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF /\ Braces
9 | Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace 41 PLF < w < 99 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF /\ Braces
10 | Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace w > 100 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF /\ Braces
11 | Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, Brace w < 40 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF / Braces
12 | Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, 41 PLF < w < 99 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF / Braces
13 | Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, Brace w > 100 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF / Braces
14 | Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, Brace w < 40 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF X Braces
15 | Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, 41 PLF < w < 99 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF X Braces
16 | Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, Brace w > 100 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF X Braces
17 | Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace w < 40 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF /\ Braces
18 | Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace 41 PLF < w < 99 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF /\ Braces
19 | Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace w > 100 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF /\ Braces
20 | Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace w < 40 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF / Braces
21 | Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF / Braces
22 | Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace w > 100 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF / Braces
23 | Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace w < 40 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF X Braces
24 | Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace 41 PLF < w < 99 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF X Braces
25 | Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace w > 100 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF X Braces
26 | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace w < 40 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF /\ Braces
27 | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace 41 PLF < w < 99 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF /\ Braces
28 | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace w > 100 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF /\ Braces
29 | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard Single Diagonal Brace, Brace w < 40 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF / Braces
30 | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF / Braces
31 | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Single Diagonal Brace, Brace w > 100 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF / Braces
32 | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace w < 40 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF X Braces
33 | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace 41 PLF < w < 99 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF X Braces
34 | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace w > 100 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF X Braces
35 | Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace w < 40 PLF | 3 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF /\ Braces
36 | Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace 41 PLF < w < 99 PLF | 3 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF /\ Braces
37 | Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace w > 100 PLF | 3 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF /\ Braces
38 | Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace w < 40 PLF | 3 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF / Braces
39 | Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | 3 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF / Braces
40 | Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace w > 100 PLF | 3 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF / Braces
41 | Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace w < 40 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF X Braces
42 | Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace 41 PLF < w < 99 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF X Braces
43 | Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace w > 100 PLF | 4 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF X Braces
44 | Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace w < 40 PLF | 3 | SDR | Costing on a per bay basis, equivalent to AISC minimum SCBF criteria. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF /\ Braces
45 | Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace 41 PLF < w < 99 PLF | 3 | SDR | Costing on a per bay basis, equivalent to AISC minimum SCBF criteria. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF /\ Braces
46 | Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace w > 100 PLF | 3 | SDR | Costing on a per bay basis, equivalent to AISC minimum SCBF criteria. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF /\ Braces
47 | Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace w < 40 PLF | 3 | SDR | Costing on a per bay basis, equivalent to AISC minimum SCBF criteria. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF / Braces
48 | Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | 3 | SDR | Costing on a per bay basis, equivalent to AISC minimum SCBF criteria. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF / Braces
49 | Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace w > 100 PLF | 3 | SDR | Costing on a per bay basis, equivalent to AISC minimum SCBF criteria. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF / Braces
50 | Special Concentric Braced Frame w double angle braces, X Brace, Brace w < 40 PLF | 3 | SDR | Costing on a per bay basis, equivalent to AISC minimum SCBF criteria. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF X Braces
51 | Special Concentric Braced Frame w double angle braces, X Brace, Brace 41 PLF < w < 99 PLF | 3 | SDR | Costing on a per bay basis, equivalent to AISC minimum SCBF criteria. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF X Braces
52 | Special Concentric Braced Frame w double angle braces, X Brace, Brace w > 100 PLF | 3 | SDR | Costing on a per bay basis, equivalent to AISC minimum SCBF criteria. Costing does not include fireproofing removal or reapplication cost. | Superstructure | SCBF X Braces
53 | Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w < 40 PLF | 3 | SDR | Costing on a per bay basis, braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | OCBF /\ Braces
54 | Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w, 41 PLF < w < 99 PLF | 3 | SDR | Costing on a per bay basis, braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | OCBF /\ Braces
55 | Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w > 100 PLF | 3 | SDR | Costing on a per bay basis, braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | OCBF /\ Braces
56 | Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w < 40 PLF | 3 | SDR | Costing on a per bay basis, braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | OCBF / Braces
57 | Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w, 41 PLF < w < 99 PLF | 3 | SDR | Costing on a per bay basis, braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | OCBF / Braces
58 | Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w > 100 PLF | 3 | SDR | Costing on a per bay basis, braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | OCBF / Braces
59 | Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w < 40 PLF | 3 | SDR | Costing on a per bay basis, braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | OCBF X Braces
60 | Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w, 41 PLF < w < 99 PLF | 3 | SDR | Costing on a per bay basis, braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | OCBF X Braces
61 | Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w > 100 PLF | 3 | SDR | Costing on a per bay basis, braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | OCBF X Braces
62 | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace w < 40 PLF | 3 | SDR | Costing on a per bay basis, equivalent to AISC OCBF criteria. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | OCBF /\ Brace
63 | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace 41 PLF < w < 99 PLF | 3 | SDR | Costing on a per bay basis, equivalent to AISC OCBF criteria. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | OCBF /\ Brace
64 | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace w > 100 PLF | 3 | SDR | Costing on a per bay basis, equivalent to AISC OCBF criteria. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | OCBF /\ Brace
65 | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace w < 40 PLF | 3 | SDR | Costing on a per bay basis, equivalent to AISC OCBF criteria. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | OCBF / Brace
66 | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | 3 | SDR | Costing on a per bay basis, equivalent to AISC OCBF criteria. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | OCBF / Brace
67 | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace w > 100 PLF | 3 | SDR | Costing on a per bay basis, equivalent to AISC OCBF criteria. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | OCBF / Brace
68 | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace w < 40 PLF | 3 | SDR | Costing on a per bay basis, equivalent to AISC OCBF criteria. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | OCBF X Brace
69 | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace 41 PLF < w < 99 PLF | 3 | SDR | Costing on a per bay basis, equivalent to AISC OCBF criteria. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | OCBF X Brace
70 | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace w > 100 PLF | 3 | SDR | Costing on a per bay basis, equivalent to AISC OCBF criteria. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | OCBF X Brace
71 | Braced frame, design for factored loads, no additional seismic detailing, Chevron Brace, Brace w < 40 PLF | 1 | SDR | Costing on a per bay basis, equivalent to current AISC R=3. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | BF /\ Brace
72 | Braced frame, design for factored loads, no additional seismic detailing, Chevron Brace, 41 PLF < w < 99 PLF | 1 | SDR | Costing on a per bay basis, equivalent to current AISC R=3. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | BF /\ Brace
73 | Braced frame, design for factored loads, no additional seismic detailing, Chevron Brace, Brace w > 100 PLF | 1 | SDR | Costing on a per bay basis, equivalent to current AISC R=3. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | BF /\ Brace
74 | Braced frame, design for factored loads, no additional seismic detailing, Single Diagonal Brace, Brace w < 40 PLF | 1 | SDR | Costing on a per bay basis, equivalent to current AISC R=3. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | BF / Brace
75 | Braced frame, design for factored loads, no additional seismic detailing, Single Diagonal Brace, 41 PLF < w < 99 PLF | 1 | SDR | Costing on a per bay basis, equivalent to current AISC R=3. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | BF / Brace
76 | Braced frame, design for factored loads, no additional seismic detailing, Single Diagonal Brace, Brace w > 100 PLF | 1 | SDR | Costing on a per bay basis, equivalent to current AISC R=3. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | BF / Brace
77 | Braced frame, design for factored loads, no additional seismic detailing, X Brace, Brace w < 40 PLF | 1 | SDR | Costing on a per bay basis, equivalent to current AISC R=3. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | BF - X Brace
78 | Braced frame, design for factored loads, no additional seismic detailing, X Brace, Brace 41 PLF < w < 99 PLF | 1 | SDR | Costing on a per bay basis, equivalent to current AISC R=3. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | BF - X Brace
79 | Braced frame, design for factored loads, no additional seismic detailing, X Brace, Brace w > 100 PLF | 1 | SDR | Costing on a per bay basis, equivalent to current AISC R=3. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Superstructure | BF - X Brace
80 | Steel Buckling Restrained Brace (BRB), Chevron Brace, Weight of brace < 40 plf. | 1 | SDR | Costing is based on 1 unit | Superstructure | Steel BRB
81 | Steel Buckling Restrained Brace (BRB), Chevron brace, Weight of brace > 41 plf and < 99 plf. | 1 | SDR | Costing is based on 1 unit | Superstructure | Steel BRB
82 | Steel Buckling Restrained Brace (BRB), Chevron Brace, Weight of brace > 100 plf. | 1 | SDR | Costing is based on 1 unit | Superstructure | Steel BRB
83 | Steel Buckling Restrained Brace (BRB), Single Diagonal Brace, Weight of brace < 40 plf. | 1 | SDR | Costing is based on 1 unit | Superstructure | Steel BRB
84 | Steel Buckling Restrained Brace (BRB), Single Diagonal brace, Weight of brace > 41 plf and < 99 plf. | 1 | SDR | Costing is based on 1 unit | Superstructure | Steel BRB
85 | Steel Buckling Restrained Brace (BRB), Single Diagonal Brace, Weight of brace > 100 plf. | 1 | SDR | Costing is based on 1 unit | Superstructure | Steel BRB
86 | Post-Northridge RBS connection with welded web, beam one side of column only, beam depth <= W27 | 3 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | RBS Connection
87 | Post-Northridge RBS connection with welded web, beam one side of column only, beam depth >= W30 | 3 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | RBS Connection
88 | Post-Northridge RBS connection with welded web, beams both sides of column, beam depth <= W27 | 3 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | RBS Connection
89 | Post-Northridge RBS connection with welded web, beams both sides of column, beam depth >= W30 | 3 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | RBS Connection
90 | Post-Northridge welded steel moment connection other than RBS, beam one side, beam depth <= W27 | 3 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | Welded Connection
91 | Post-Northridge welded steel moment connection other than RBS, beam one side, beam depth >= W30 | 3 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | Welded Connection
92 | Post-Northridge welded steel moment connection other than RBS, beams both sides, beam depth <= W27 | 3 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | Welded Connection
93 | Post-Northridge welded steel moment connection other than RBS, beams both sides, beam depth >= W30 | 3 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | Welded Connection
94 | Pre-Northridge WUF-B beam-column joint, beam one side of column, beam depth <= W27 | 5 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | WUF-B Connection
95 | Pre-Northridge WUF-B beam-column joint, beam one side of column, beam depth >= W30 | 5 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | WUF-B Connection
96 | Pre-Northridge WUF-B beam-column joint, beam both sides of column, beam depth <= W27 | 5 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | WUF-B Connection
97 | Pre-Northridge WUF-B beam-column joint, beam both sides of column, beam depth >= W30 | 5 | SDR | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | WUF-B Connection
98 | EBF Shear Link, no floor beams, link w < 100 PLF | 3 | LINK ROT | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | EBF Shear Link
99 | EBF Shear Link, no floor beams, link w < 200 PLF | 3 | LINK ROT | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | EBF Shear Link
100 | EBF Shear Link, with floor beams, link w < 100 PLF | 3 | LINK ROT | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | EBF Shear Link
101 | EBF Shear Link, with floor beams, link w < 200 PLF | 3 | LINK ROT | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Superstructure | EBF Shear Link
102 | ACI 318 SMF , Conc Col & Bm = 24 x 24", Beam one side" | 4 | SDR | ACI318 Concrete SMF, ductile response. Meets the requirements of ACI318 SMF. Costing is on a per joint basis. | Superstructure | ACI 318 SMF
103 | ACI 318 SMF , Conc Col & Bm = 24 x 24", Beam both sides" | 4 | SDR | ACI318 Concrete SMF, ductile response. Meets the requirements of ACI318 SMF. Costing is on a per joint basis. | Superstructure | ACI 318 SMF
104 | ACI 318 SMF , Conc Col & Bm = 24 x 36", Beam one side" | 4 | SDR | ACI318 Concrete SMF, ductile response. Meets the requirements of ACI318 SMF. Costing is on a per joint basis. | Superstructure | ACI 318 SMF
105 | ACI 318 SMF , Conc Col & Bm = 24 x 36", Beam both sides" | 4 | SDR | ACI318 Concrete SMF, ductile response. Meets the requirements of ACI318 SMF. Costing is on a per joint basis. | Superstructure | ACI 318 SMF
106 | ACI 318 SMF , Conc Col & Bm = 36 x 36", Beam one side" | 4 | SDR | ACI318 Concrete SMF, ductile response. Meets the requirements of ACI318 SMF. Costing is on a per joint basis. | Superstructure | ACI 318 SMF
107 | ACI 318 SMF , Conc Col & Bm = 36 x 36", Beam both sides" | 4 | SDR | ACI318 Concrete SMF, ductile response. Meets the requirements of ACI318 SMF. Costing is on a per joint basis. | Superstructure | ACI 318 SMF
108 | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24 x 24", Beam one side" | 4 | SDR | Non-conforming SMF, joint shear damage, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Column Pu < 0.6f'cAg, (3) Column flexural response with HIGH ductility, (4) Beam compliant transverse reinforcing with low beam V/bwd(f'c)^0.5, (5) Joints with compliant transverse reinforcing details with spacing < d(column)/2 and Joint V/Vn < 1.2. Costing is on a per joint basis. | Superstructure | MF with SMF
109 | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24 x 24", Beam both sides" | 4 | SDR | Non-conforming SMF, joint shear damage, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Column Pu < 0.6f'cAg, (3) Column flexural response with HIGH ductility, (4) Beam compliant transverse reinforcing with low beam V/bwd(f'c)^0.5, (5) Joints with compliant transverse reinforcing details with spacing < d(column)/2 and Joint V/Vn < 1.2. Costing is on a per joint basis. | Superstructure | MF with SMF
110 | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24 x 36", Beam one side" | 4 | SDR | Non-conforming SMF, joint shear damage, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Column Pu < 0.6f'cAg, (3) Column flexural response with HIGH ductility, (4) Beam compliant transverse reinforcing with low beam V/bwd(f'c)^0.5, (5) Joints with compliant transverse reinforcing details with spacing < d(column)/2 and Joint V/Vn < 1.2. Costing is on a per joint basis. | Superstructure | MF with SMF
111 | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24 x 36", Beam both sides" | 4 | SDR | Non-conforming SMF, joint shear damage, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Column Pu < 0.6f'cAg, (3) Column flexural response with HIGH ductility, (4) Beam compliant transverse reinforcing with low beam V/bwd(f'c)^0.5, (5) Joints with compliant transverse reinforcing details with spacing < d(column)/2 and Joint V/Vn < 1.2. Costing is on a per joint basis. | Superstructure | MF with SMF
112 | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 36 x 36", Beam one side" | 4 | SDR | Non-conforming SMF, joint shear damage, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Column Pu < 0.6f'cAg, (3) Column flexural response with HIGH ductility, (4) Beam compliant transverse reinforcing with low beam V/bwd(f'c)^0.5, (5) Joints with compliant transverse reinforcing details with spacing < d(column)/2 and Joint V/Vn < 1.2. Costing is on a per joint basis. | Superstructure | MF with SMF
113 | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 36 x 36", Beam both sides" | 4 | SDR | Non-conforming SMF, joint shear damage, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Column Pu < 0.6f'cAg, (3) Column flexural response with HIGH ductility, (4) Beam compliant transverse reinforcing with low beam V/bwd(f'c)^0.5, (5) Joints with compliant transverse reinforcing details with spacing < d(column)/2 and Joint V/Vn < 1.2. Costing is on a per joint basis. | Superstructure | MF with SMF
114 | ACI 318 IMF, Conc Col & Bm = 24 x 24", Beam one side" | 4 | SDR | ACI318 IMF, joint shear damage or failure, beam or column flexure-shear response. Meets the following requirements: (1) Column Pu < 0.3Agf'c Costing is on a per joint basis. | Superstructure | ACI 318 IMF
115 | ACI 318 IMF, Conc Col & Bm = 24 x 24", Beam both sides" | 4 | SDR | ACI318 IMF, joint shear damage or failure, beam or column flexure-shear response. Meets the following requirements: (1) Column Pu < 0.3Agf'c Costing is on a per joint basis. | Superstructure | ACI 318 IMF
116 | ACI 318 IMF, Conc Col & Bm = 24 x 36", Beam one side" | 4 | SDR | ACI318 IMF, joint shear damage or failure, beam or column flexure-shear response. Meets the following requirements: (1) Column Pu < 0.3Agf'c Costing is on a per joint basis. | Superstructure | ACI 318 IMF
117 | ACI 318 IMF, Conc Col & Bm = 24 x 36", Beam both sides" | 4 | SDR | ACI318 IMF, joint shear damage or failure, beam or column flexure-shear response. Meets the following requirements: (1) Column Pu < 0.3Agf'c Costing is on a per joint basis. | Superstructure | ACI 318 IMF
118 | ACI 318 IMF, Conc Col & Bm = 36 x 36", Beam one side" | 4 | SDR | ACI318 IMF, joint shear damage or failure, beam or column flexure-shear response. Meets the following requirements: (1) Column Pu < 0.3Agf'c Costing is on a per joint basis. | Superstructure | ACI 318 IMF
119 | ACI 318 IMF, Conc Col & Bm = 36 x 36", Beam both sides" | 4 | SDR | ACI318 IMF, joint shear damage or failure, beam or column flexure-shear response. Meets the following requirements: (1) Column Pu < 0.3Agf'c Costing is on a per joint basis. | Superstructure | ACI 318 IMF
120 | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24 x 24", Beam one side" | 3 | SDR | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Superstructure | ACI 318 OMF
121 | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24 x 24", Beam both sides" | 3 | SDR | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Superstructure | ACI 318 OMF
122 | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24 x 36", Beam one side" | 3 | SDR | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Superstructure | ACI 318 OMF
123 | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24 x 36", Beam both sides" | 3 | SDR | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Superstructure | ACI 318 OMF
124 | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 36 x 36", Beam one side" | 3 | SDR | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Superstructure | ACI 318 OMF
125 | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 36 x 36", Beam both sides" | 3 | SDR | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Superstructure | ACI 318 OMF
126 | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24 x 24", Beam one side" | 3 | SDR | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Superstructure | ACI 318 OMF
127 | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24 x 24", Beam both sides" | 3 | SDR | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Superstructure | ACI 318 OMF
128 | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24 x 36", Beam one side" | 3 | SDR | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Superstructure | ACI 318 OMF
129 | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24 x 36", Beam both sides" | 3 | SDR | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Superstructure | ACI 318 OMF
130 | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 36 x 36", Beam one side" | 3 | SDR | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Superstructure | ACI 318 OMF
131 | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 36 x 36", Beam both sides" | 3 | SDR | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Superstructure | ACI 318 OMF
132 | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24 x 24", Beam one side" | 3 | SDR | ACI318 OMF, beam flexure-shear or shear failure, beam flexural response. Meets the following requirements: (1) Beam Vn < Veq. Costing is on a per joint basis. | Superstructure | ACI 318 OMF
133 | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24 x 24", Beam both sides" | 3 | SDR | ACI318 OMF, beam flexure-shear or shear failure, beam flexural response. Meets the following requirements: (1) Beam Vn < Veq. Costing is on a per joint basis. | Superstructure | ACI 318 OMF
134 | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24 x 36", Beam one side" | 3 | SDR | ACI318 OMF, beam flexure-shear or shear failure, beam flexural response. Meets the following requirements: (1) Beam Vn < Veq. Costing is on a per joint basis. | Superstructure | ACI 318 OMF
135 | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24 x 36", Beam both sides" | 3 | SDR | ACI318 OMF, beam flexure-shear or shear failure, beam flexural response. Meets the following requirements: (1) Beam Vn < Veq. Costing is on a per joint basis. | Superstructure | ACI 318 OMF
136 | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 36 x 36", Beam one side" | 3 | SDR | ACI318 OMF, beam flexure-shear or shear failure, beam flexural response. Meets the following requirements: (1) Beam Vn < Veq. Costing is on a per joint basis. | Superstructure | ACI 318 OMF
137 | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 36 x 36", Beam both sides" | 3 | SDR | ACI318 OMF, beam flexure-shear or shear failure, beam flexural response. Meets the following requirements: (1) Beam Vn < Veq. Costing is on a per joint basis. | Superstructure | ACI 318 OMF
138 | ACI 318 OMF with weak columns, Conc Col & Bm = 24 x 24", Beam one side" | 3 | SDR | ACI318 OMF, column shear or flexural-shear failure, column flexural response. Meets the following requirements: (1) Column Pu < 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Superstructure | ACI 318 OMF
139 | ACI 318 OMF with weak columns, Conc Col & Bm = 24 x 24", Beam both sides" | 3 | SDR | ACI318 OMF, column shear or flexural-shear failure, column flexural response. Meets the following requirements: (1) Column Pu < 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Superstructure | ACI 318 OMF
140 | ACI 318 OMF with weak columns, Conc Col & Bm = 24 x 36", Beam one side" | 3 | SDR | ACI318 OMF, column shear or flexural-shear failure, column flexural response. Meets the following requirements: (1) Column Pu < 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Superstructure | ACI 318 OMF
141 | ACI 318 OMF with weak columns, Conc Col & Bm = 24 x 36", Beam both sides" | 3 | SDR | ACI318 OMF, column shear or flexural-shear failure, column flexural response. Meets the following requirements: (1) Column Pu < 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Superstructure | ACI 318 OMF
142 | ACI 318 OMF with weak columns, Conc Col & Bm = 36 x 36", Beam one side" | 3 | SDR | ACI318 OMF, column shear or flexural-shear failure, column flexural response. Meets the following requirements: (1) Column Pu < 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Superstructure | ACI 318 OMF
143 | ACI 318 OMF with weak columns, Conc Col & Bm = 36 x 36", Beam both sides" | 3 | SDR | ACI318 OMF, column shear or flexural-shear failure, column flexural response. Meets the following requirements: (1) Column Pu < 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Superstructure | ACI 318 OMF
144 | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24 x 24", Beam one side" | 2 | SDR | ACI318 OMF, column flexure, flexural-shear, or shear failure at high axial load. Column flexural-shear response. Meets the following requirements: (1) Column Pu > 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Superstructure | ACI 318 OMF
145 | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24 x 24", Beam both sides" | 2 | SDR | ACI318 OMF, column flexure, flexural-shear, or shear failure at high axial load. Column flexural-shear response. Meets the following requirements: (1) Column Pu > 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Superstructure | ACI 318 OMF
146 | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24 x 36", Beam one side" | 2 | SDR | ACI318 OMF, column flexure, flexural-shear, or shear failure at high axial load. Column flexural-shear response. Meets the following requirements: (1) Column Pu > 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Superstructure | ACI 318 OMF
147 | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24 x 36", Beam both sides" | 2 | SDR | ACI318 OMF, column flexure, flexural-shear, or shear failure at high axial load. Column flexural-shear response. Meets the following requirements: (1) Column Pu > 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Superstructure | ACI 318 OMF
148 | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 36 x 36", Beam one side" | 2 | SDR | ACI318 OMF, column flexure, flexural-shear, or shear failure at high axial load. Column flexural-shear response. Meets the following requirements: (1) Column Pu > 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Superstructure | ACI 318 OMF
149 | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 36 x 36", Beam both sides" | 2 | SDR | ACI318 OMF, column flexure, flexural-shear, or shear failure at high axial load. Column flexural-shear response. Meets the following requirements: (1) Column Pu > 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Superstructure | ACI 318 OMF
150 | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24 x 24", Beam one side" | 3 | SDR | Non-Conforming MF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) ASCE41 non-compliant joint transverse reinforcing and or joint V/Vn > 1.2, (3) IGH beam ductility per ASCE41-06 Table 6-7i, (4) Compliant beam transverse reinforcing with LOW beam V / bwd(f'c)^0.5. Costing is on a per joint basis. | Superstructure | RC MF
151 | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24 x 24", Beam both sides" | 3 | SDR | Non-Conforming MF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) ASCE41 non-compliant joint transverse reinforcing and or joint V/Vn > 1.2, (3) IGH beam ductility per ASCE41-06 Table 6-7i, (4) Compliant beam transverse reinforcing with LOW beam V / bwd(f'c)^0.5. Costing is on a per joint basis. | Superstructure | RC MF
152 | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24 x 36", Beam one side" | 3 | SDR | Non-Conforming MF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) ASCE41 non-compliant joint transverse reinforcing and or joint V/Vn > 1.2, (3) IGH beam ductility per ASCE41-06 Table 6-7i, (4) Compliant beam transverse reinforcing with LOW beam V / bwd(f'c)^0.5. Costing is on a per joint basis. | Superstructure | RC MF
153 | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24 x 36", Beam both sides" | 3 | SDR | Non-Conforming MF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) ASCE41 non-compliant joint transverse reinforcing and or joint V/Vn > 1.2, (3) IGH beam ductility per ASCE41-06 Table 6-7i, (4) Compliant beam transverse reinforcing with LOW beam V / bwd(f'c)^0.5. Costing is on a per joint basis. | Superstructure | RC MF
154 | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 36 x 36", Beam one side" | 3 | SDR | Non-Conforming MF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) ASCE41 non-compliant joint transverse reinforcing and or joint V/Vn > 1.2, (3) IGH beam ductility per ASCE41-06 Table 6-7i, (4) Compliant beam transverse reinforcing with LOW beam V / bwd(f'c)^0.5. Costing is on a per joint basis. | Superstructure | RC MF
155 | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 36 x 36", Beam both sides" | 3 | SDR | Non-Conforming MF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) ASCE41 non-compliant joint transverse reinforcing and or joint V/Vn > 1.2, (3) IGH beam ductility per ASCE41-06 Table 6-7i, (4) Compliant beam transverse reinforcing with LOW beam V / bwd(f'c)^0.5. Costing is on a per joint basis. | Superstructure | RC MF
156 | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24 x 24", Beam one side" | 3 | SDR | Non-Conforming MF, joint shear failure, column flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam < 0.8, (2) [...TBD…], (3) Non-compliant column transverse reinforcement and or joint V/Vn > 1.2 Costing is on a per joint basis. | Superstructure | RC MF
157 | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24 x 24", Beam both sides" | 3 | SDR | Non-Conforming MF, joint shear failure, column flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam < 0.8, (2) [...TBD…], (3) Non-compliant column transverse reinforcement and or joint V/Vn > 1.2 Costing is on a per joint basis. | Superstructure | RC MF
158 | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24 x 36", Beam one side" | 3 | SDR | Non-Conforming MF, joint shear failure, column flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam < 0.8, (2) [...TBD…], (3) Non-compliant column transverse reinforcement and or joint V/Vn > 1.2 Costing is on a per joint basis. | Superstructure | RC MF
159 | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24 x 36", Beam both sides" | 3 | SDR | Non-Conforming MF, joint shear failure, column flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam < 0.8, (2) [...TBD…], (3) Non-compliant column transverse reinforcement and or joint V/Vn > 1.2 Costing is on a per joint basis. | Superstructure | RC MF
160 | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 36 x 36", Beam one side" | 3 | SDR | Non-Conforming MF, joint shear failure, column flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam < 0.8, (2) [...TBD…], (3) Non-compliant column transverse reinforcement and or joint V/Vn > 1.2 Costing is on a per joint basis. | Superstructure | RC MF
161 | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 36 x 36", Beam both sides" | 3 | SDR | Non-Conforming MF, joint shear failure, column flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam < 0.8, (2) [...TBD…], (3) Non-compliant column transverse reinforcement and or joint V/Vn > 1.2 Costing is on a per joint basis. | Superstructure | RC MF
162 | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24 x 24", Beam one side" | 3 | SDR | Non-Conforming MF, beam shear failure, beam flexural response. Meets the following requirements: (1) Beam with HIGH V/bwd(f'c)^0.5 or non-compliant transverse beam reinforcing. Costing is on a per joint basis. | Superstructure | RC MF
163 | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24 x 24", Beam both sides" | 3 | SDR | Non-Conforming MF, beam shear failure, beam flexural response. Meets the following requirements: (1) Beam with HIGH V/bwd(f'c)^0.5 or non-compliant transverse beam reinforcing. Costing is on a per joint basis. | Superstructure | RC MF
164 | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24 x 36", Beam one side" | 3 | SDR | Non-Conforming MF, beam shear failure, beam flexural response. Meets the following requirements: (1) Beam with HIGH V/bwd(f'c)^0.5 or non-compliant transverse beam reinforcing. Costing is on a per joint basis. | Superstructure | RC MF
165 | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24 x 36", Beam both sides" | 3 | SDR | Non-Conforming MF, beam shear failure, beam flexural response. Meets the following requirements: (1) Beam with HIGH V/bwd(f'c)^0.5 or non-compliant transverse beam reinforcing. Costing is on a per joint basis. | Superstructure | RC MF
166 | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 36 x 36", Beam one side" | 3 | SDR | Non-Conforming MF, beam shear failure, beam flexural response. Meets the following requirements: (1) Beam with HIGH V/bwd(f'c)^0.5 or non-compliant transverse beam reinforcing. Costing is on a per joint basis. | Superstructure | RC MF
167 | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 36 x 36", Beam both sides" | 3 | SDR | Non-Conforming MF, beam shear failure, beam flexural response. Meets the following requirements: (1) Beam with HIGH V/bwd(f'c)^0.5 or non-compliant transverse beam reinforcing. Costing is on a per joint basis. | Superstructure | RC MF
168 | Non-conforming MF, weak columns, Conc Col & Bm = 24 x 24", Beam one side" | 3 | SDR | Non-Conforming MF, column flexure-shear or shear failure, column flexural response. Meets the following requirements: (1) […TBD…] Costing is on a per joint basis. | Superstructure | RC MF
169 | Non-conforming MF, weak columns, Conc Col & Bm = 24 x 24", Beam both sides" | 3 | SDR | Non-Conforming MF, column flexure-shear or shear failure, column flexural response. Meets the following requirements: (1) […TBD…] Costing is on a per joint basis. | Superstructure | RC MF
170 | Non-conforming MF, weak columns, Conc Col & Bm = 24 x 36", Beam one side" | 3 | SDR | Non-Conforming MF, column flexure-shear or shear failure, column flexural response. Meets the following requirements: (1) […TBD…] Costing is on a per joint basis. | Superstructure | RC MF
171 | Non-conforming MF, weak columns, Conc Col & Bm = 24 x 36", Beam both sides" | 3 | SDR | Non-Conforming MF, column flexure-shear or shear failure, column flexural response. Meets the following requirements: (1) […TBD…] Costing is on a per joint basis. | Superstructure | RC MF
172 | Non-conforming MF, weak columns, Conc Col & Bm = 36 x 36", Beam one side" | 3 | SDR | Non-Conforming MF, column flexure-shear or shear failure, column flexural response. Meets the following requirements: (1) […TBD…] Costing is on a per joint basis. | Superstructure | RC MF
173 | Non-conforming MF, weak columns, Conc Col & Bm = 36 x 36", Beam both sides" | 3 | SDR | Non-Conforming MF, column flexure-shear or shear failure, column flexural response. Meets the following requirements: (1) […TBD…] Costing is on a per joint basis. | Superstructure | RC MF
174 | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24 x 24", Beam both sides" | 2 | SDR | Non-Conforming MF, column flexure, flexure-shear, or shear failure, column flexural response. Meets the following requirements: (1) Column Pu > 0.6f'cAg, (2) Column Vn < Veq Costing is on a per joint basis. | Superstructure | RC MF
175 | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24 x 24", Beam one side" | 2 | SDR | Non-Conforming MF, column flexure, flexure-shear, or shear failure, column flexural response. Meets the following requirements: (1) Column Pu > 0.6f'cAg, (2) Column Vn < Veq Costing is on a per joint basis. | Superstructure | RC MF
176 | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24 x 36", Beam one side" | 2 | SDR | Non-Conforming MF, column flexure, flexure-shear, or shear failure, column flexural response. Meets the following requirements: (1) Column Pu > 0.6f'cAg, (2) Column Vn < Veq Costing is on a per joint basis. | Superstructure | RC MF
177 | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24 x 36", Beam both sides" | 2 | SDR | Non-Conforming MF, column flexure, flexure-shear, or shear failure, column flexural response. Meets the following requirements: (1) Column Pu > 0.6f'cAg, (2) Column Vn < Veq Costing is on a per joint basis. | Superstructure | RC MF
178 | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 36 x 36", Beam one side" | 2 | SDR | Non-Conforming MF, column flexure, flexure-shear, or shear failure, column flexural response. Meets the following requirements: (1) Column Pu > 0.6f'cAg, (2) Column Vn < Veq Costing is on a per joint basis. | Superstructure | RC MF
179 | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 36 x 36", Beam both sides" | 2 | SDR | Non-Conforming MF, column flexure, flexure-shear, or shear failure, column flexural response. Meets the following requirements: (1) Column Pu > 0.6f'cAg, (2) Column Vn < Veq Costing is on a per joint basis. | Superstructure | RC MF
180 | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24 x 24", Beam one side" | 2 | SDR | Non-Conforming MF, non-ductile failure, non-ductile response. May exhibit the following: (1) Splice detailing or length inadequate per ASCE 41-06 Table 6-7iii, (2) Beam or column reinforcing spliced at the face of joint, (3) Beam longitudinal steel discontinuous through joint per ASCE41-06 Table 6-7iii. Costing is on a per joint basis. | Superstructure | RC MF
181 | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24 x 24", Beam both sides" | 2 | SDR | Non-Conforming MF, non-ductile failure, non-ductile response. May exhibit the following: (1) Splice detailing or length inadequate per ASCE 41-06 Table 6-7iii, (2) Beam or column reinforcing spliced at the face of joint, (3) Beam longitudinal steel discontinuous through joint per ASCE41-06 Table 6-7iii. Costing is on a per joint basis. | Superstructure | RC MF
182 | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24 x 36", Beam one side" | 2 | SDR | Non-Conforming MF, non-ductile failure, non-ductile response. May exhibit the following: (1) Splice detailing or length inadequate per ASCE 41-06 Table 6-7iii, (2) Beam or column reinforcing spliced at the face of joint, (3) Beam longitudinal steel discontinuous through joint per ASCE41-06 Table 6-7iii. Costing is on a per joint basis. | Superstructure | RC MF
183 | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24 x 36", Beam both sides" | 2 | SDR | Non-Conforming MF, non-ductile failure, non-ductile response. May exhibit the following: (1) Splice detailing or length inadequate per ASCE 41-06 Table 6-7iii, (2) Beam or column reinforcing spliced at the face of joint, (3) Beam longitudinal steel discontinuous through joint per ASCE41-06 Table 6-7iii. Costing is on a per joint basis. | Superstructure | RC MF
184 | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 36 x 36", Beam one side" | 2 | SDR | Non-Conforming MF, non-ductile failure, non-ductile response. May exhibit the following: (1) Splice detailing or length inadequate per ASCE 41-06 Table 6-7iii, (2) Beam or column reinforcing spliced at the face of joint, (3) Beam longitudinal steel discontinuous through joint per ASCE41-06 Table 6-7iii. Costing is on a per joint basis. | Superstructure | RC MF
185 | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 36 x 36", Beam both sides" | 2 | SDR | Non-Conforming MF, non-ductile failure, non-ductile response. May exhibit the following: (1) Splice detailing or length inadequate per ASCE 41-06 Table 6-7iii, (2) Beam or column reinforcing spliced at the face of joint, (3) Beam longitudinal steel discontinuous through joint per ASCE41-06 Table 6-7iii. Costing is on a per joint basis. | Superstructure | RC MF
186 | Rectangular low aspect ratio concrete walls 8 or less thick single curtain up to 15' high" | 3 | SDR | Costing for each 144 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | Concrete Wall
187 | Rectangular low aspect ratio concrete walls 8 or less thick single curtain 16' high to 24' high" | 3 | SDR | Costing for each 400 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | Concrete Wall
188 | Rectangular low aspect ratio concrete walls 8 or less thick single curtain 25' high to 40' high" | 3 | SDR | Costing for each 900 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | Concrete Wall
189 | Rectangular low aspect ratio concrete walls 8-16" double curtain; with heights of up to 15'" | 3 | SDR | Costing for each 144 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | Concrete Wall
190 | Rectangular low aspect ratio concrete walls 8-16" double curtain; with heights of 16' to 24'" | 3 | SDR | Costing for each 400 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | Concrete Wall
191 | Rectangular low aspect ratio concrete walls 8-16" double curtain; with heights of 24' to 40'" | 3 | SDR | Costing for each 900 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | Concrete Wall
192 | Rectangular low aspect ratio concrete walls 18-24" thick with double curtain and heights up to 15' " | 3 | SDR | Costing for each 144 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | Concrete Wall
193 | Rectangular low aspect ratio concrete walls 18-24" thick with double curtain and heights 16' - 24' " | 3 | SDR | Costing for each 400 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | Concrete Wall
194 | Rectangular low aspect ratio concrete walls 18-24" thick with double curtain and heights 25' - 40' " | 3 | SDR | Costing for each 900 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | Concrete Wall
195 | Low-rise reinforced concrete walls with return flanges, less than 8 thick up to 15' high" | 2 | SDR | Costing for each 144 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | RC Wall
196 | Low-rise reinforced concrete walls with return flanges, less than 8 thick, 16' to 24' high" | 2 | SDR | Costing for each 400 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | RC Wall
197 | Low-rise reinforced concrete walls with return flanges, less than 8 thick, 25' to 40' high" | 2 | SDR | Costing for each 900 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | RC Wall
198 | Low-rise reinforced concrete walls with return flanges, 8 to 16" thick up to 15' high" | 2 | SDR | Costing for each 144 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | RC Wall
199 | Low-rise reinforced concrete walls with return flanges, 8 to 16" thick, 16' to 24' high" | 2 | SDR | Costing for each 400 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | RC Wall
200 | Low-rise reinforced concrete walls with return flanges, 8 to 16" thick, 25' to 40' high" | 2 | SDR | Costing for each 900 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | RC Wall
201 | Low-rise reinforced concrete walls with return flanges, 17 to 24" thick" up to 15' high" | 2 | SDR | Costing for each 144 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | RC Wall
202 | Low-rise reinforced concrete walls with return flanges, 17 to 24" thick, 16' to 24' high" | 2 | SDR | Costing for each 400 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | RC Wall
203 | Low-rise reinforced concrete walls with return flanges, 17 to 24" thick, 25' to 40' high" | 2 | SDR | Costing for each 900 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | RC Wall
204 | Low rise reinforced concrete walls with boundary columns, less than 8 thick, height <15'" | 2 | SDR | Costing for each 144 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | RC Wall
205 | Low rise reinforced concrete walls with boundary columns, less than 8 thick, height between 16'-24'" | 2 | SDR | Costing for each 400 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | RC Wall
206 | Low rise reinforced concrete walls with boundary columns, less than 8 thick, height between 24'-40'" | 2 | SDR | Costing for each 900 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | RC Wall
207 | Low rise reinforced concrete walls with boundary columns, 8 to 16" thick, height <15'" | 2 | SDR | Costing for each 144 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | RC Wall
208 | Low rise reinforced concrete walls with boundary columns, 8 to 16" thick, height between 16'-24'" | 2 | SDR | Costing for each 400 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | RC Wall
209 | Low rise reinforced concrete walls with boundary columns, 8 to 16" thick, height between 24'-40'" | 2 | SDR | Costing for each 900 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | RC Wall
210 | Low rise reinforced concrete walls with boundary columns, 17-24" thick, height <15'" | 2 | SDR | Costing for each 144 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | RC Wall
211 | Low rise reinforced concrete walls with boundary columns, 17-24" thick, height between 16'-24'" | 2 | SDR | Costing for each 400 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | RC Wall
212 | Low rise reinforced concrete walls with boundary columns, 17-24" thick, height between 24'-40'" | 2 | SDR | Costing for each 900 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Superstructure | RC Wall
213 | Slender Concrete Wall, 12 thick, 12' high, 15' long" | 3 | ED | Slender concrete shear wall with aspect ratio greater than or equal to 2.0. Costing assumes a 144 ft^2 wall panel. | Superstructure | Concrete Wall
214 | Slender Concrete Wall, 12 thick, 12' high, 20' long" | 3 | ED | Slender concrete shear wall with aspect ratio greater than or equal to 2.0. Costing assumes a 144 ft^2 wall panel. | Superstructure | Concrete Wall
215 | Slender Concrete Wall, 12 thick, 12' high, 30' long" | 3 | ED | Slender concrete shear wall with aspect ratio greater than or equal to 2.0. Costing assumes a 144 ft^2 wall panel. | Superstructure | Concrete Wall
216 | Slender Concrete Wall, 18 thick, 12' high, 15' long" | 3 | ED | Slender concrete shear wall with aspect ratio greater than or equal to 2.0. Costing assumes a 144 ft^2 wall panel. | Superstructure | Concrete Wall
217 | Slender Concrete Wall, 18 thick, 12' high, 20' long" | 3 | ED | Slender concrete shear wall with aspect ratio greater than or equal to 2.0. Costing assumes a 144 ft^2 wall panel. | Superstructure | Concrete Wall
218 | Slender Concrete Wall, 18 thick, 12' high, 30' long" | 3 | ED | Slender concrete shear wall with aspect ratio greater than or equal to 2.0. Costing assumes a 144 ft^2 wall panel. | Superstructure | Concrete Wall
219 | Slender Concrete Wall, 30 thick, 12' high, 15' long" | 3 | ED | Slender concrete shear wall with aspect ratio greater than or equal to 2.0. Costing assumes a 144 ft^2 wall panel. | Superstructure | Concrete Wall
220 | Slender Concrete Wall, 30 thick, 12' high, 20' long" | 3 | ED | Slender concrete shear wall with aspect ratio greater than or equal to 2.0. Costing assumes a 144 ft^2 wall panel. | Superstructure | Concrete Wall
221 | Slender Concrete Wall, 30 thick, 12' high, 30' long" | 3 | ED | Slender concrete shear wall with aspect ratio greater than or equal to 2.0. Costing assumes a 144 ft^2 wall panel. | Superstructure | Concrete Wall
222 | Reinforced concrete flat slabs- columns without shear reinforcing 0<Vg/Vo<.2, no continuity reinf | 2 | SDR | Costing per joint, minimum of 6" thick slab, maximum of 12" thick slab. | Superstructure | RC Flat Slab
223 | Reinforced concrete flat slabs- columns without shear reinforcing 0<Vg/Vo<.2, with continuity reinf | 2 | SDR | Costing per joint, minimum of 6" thick slab, maximum of 12" thick slab. | Superstructure | RC Flat Slab
224 | Reinforced concrete flat slabs- columns without shear reinforcing .2<Vg/Vo<.4, no continuity reinf | 2 | SDR | Costing is on a per joint basis. | Superstructure | RC Flat Slab
225 | Reinforced concrete flat slabs- columns without shear reinforcing .2<Vg/Vo<.4, with continuity reinf | 2 | SDR | Costing is on a per joint basis. | Superstructure | RC Flat Slab
226 | Reinforced concrete flat slabs- columns without shear reinforcing .4<Vg/Vo<.6, no continuity reinf | 2 | SDR | Costing is on a per joint basis. | Superstructure | RC Flat Slab
227 | Reinforced concrete flat slabs- columns without shear reinforcing .4<Vg/Vo<.6, with continuity reinf | 2 | SDR | Costing is on a per joint basis. | Superstructure | RC Flat Slab
228 | Reinforced concrete flat slabs- columns with shear reinforcing 0.2<Vg/Vo<0.4 | 2 | SDR | Costing is on a per joint basis. | Superstructure | RC Flat Slab
229 | Reinforced concrete flat slabs- columns with shear reinforcing 0.4<Vg/Vo<.6 | 2 | SDR | Costing is on a per joint basis. | Superstructure | RC Flat Slab
230 | Post-tensioned concrete flat slabs- columns without shear reinforcing 0.2<Vg/Vo<.0.4, no continuity reinf | 2 | SDR | Costing is on a per joint basis. | Superstructure | Post-Tensioned Flat Slab
231 | Post-tensioned concrete flat slabs- columns without shear reinforcing 0.2<Vg/Vo<.0.4, with continuity reinf | 2 | SDR | Costing is on a per joint basis. | Superstructure | Post-Tensioned Flat Slab
232 | Post-tensioned concrete flat slabs- columns without shear reinforcing 0.4<Vg/Vo<.0.6, no continuity reinf | 2 | SDR | Costing is on a per joint basis. | Superstructure | Post-Tensioned Flat Slab
233 | Post-tensioned concrete flat slabs- columns without shear reinforcing 0.4<Vg/Vo<.0.6, with continuity reinf | 2 | SDR | Costing is on a per joint basis. | Superstructure | Post-Tensioned Flat Slab
234 | Post-tensioned concrete flat slabs- columns with shear reinforcing 0<Vg/Vo<.0.4 | 2 | SDR | Costing is on a per joint basis. | Superstructure | Post-Tensioned Flat Slab
235 | Post-tensioned concrete flat slabs- columns with shear reinforcing 0.4<Vg/Vo<.0.6 | 2 | SDR | Costing is on a per joint basis. | Superstructure | Post-Tensioned Flat Slab
236 | Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0<Vg/Vo<0.4, no continuity reinf | 2 | SDR | Costing is on a per joint basis. | Superstructure | RC Flat Slab
237 | Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0<Vg/Vo<0.4, with continuity reinf | 2 | SDR | Costing is on a per joint basis. | Superstructure | RC Flat Slab
238 | Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0.4<Vg/Vo<0.6, no continuity reinf | 2 | SDR | Costing is on a per joint basis. | Superstructure | RC Flat Slab
239 | Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0.4<Vg/Vo<0.6, with continuity reinf | 2 | SDR | Costing is on a per joint basis. | Superstructure | RC Flat Slab
240 | Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam < 16 wide and depth < 30"" | 3 | LINK BEAM ROT | Costing is based on 1 unit | Superstructure | Link Beam
241 | Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam < 16 wide and depth < 30"" | 3 | LINK BEAM ROT | Costing is based on 1 unit | Superstructure | Link Beam
242 | Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam < 16 wide and depth < 30"" | 3 | LINK BEAM ROT | Costing is based on 1 unit | Superstructure | Link Beam
243 | Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam < 16 wide and depth < 30"" | 3 | LINK BEAM ROT | Costing is based on 1 unit | Superstructure | Link Beam
244 | Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam > 16 wide and depth < 30"" | 3 | LINK BEAM ROT | Costing is based on 1 unit | Superstructure | Link Beam
245 | Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam > 16 wide and depth < 30"" | 3 | LINK BEAM ROT | Costing is based on 1 unit | Superstructure | Link Beam
246 | Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam > 16 wide and depth < 30"" | 3 | LINK BEAM ROT | Costing is based on 1 unit | Superstructure | Link Beam
247 | Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam > 16 wide and depth < 30"" | 3 | LINK BEAM ROT | Costing is based on 1 unit | Superstructure | Link Beam
248 | Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam > 24 wide and depth < 30"" | 3 | LINK BEAM ROT | Costing is based on 1 unit | Superstructure | Link Beam
249 | Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam > 24 wide and depth < 30"" | 3 | LINK BEAM ROT | Costing is based on 1 unit | Superstructure | Link Beam
250 | Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam > 24 wide and depth < 30"" | 3 | LINK BEAM ROT | Costing is based on 1 unit | Superstructure | Link Beam
251 | Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam > 24 wide and depth < 30"" | 3 | LINK BEAM ROT | Costing is based on 1 unit | Superstructure | Link Beam
252 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 4 to 6"' thick, up to 12 foot tall" | 2 | SDR | Costing for each 100 ft^2 Wall Panel | Superstructure | Masonry Wall
253 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 4 to 6"' thick, greater than 12 foot tall" | 2 | SDR | Costing for each 225 ft^2 Wall Panel | Superstructure | Masonry Wall
254 | Ordinary reinforced masonry walls with partially grouted cells, 4 to 6" thick, flexure dominated up to 12' tall" | 3 | SDR | Costing for each 100 ft^2 Wall Panel | Superstructure | Masonry Wall
255 | Ordinary reinforced masonry walls with partially grouted cells, 4 to 6" thick, flexure dominated greater than 12' tall" | 3 | SDR | Costing for each 225 ft^2 Wall Panel | Superstructure | Masonry Wall
256 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 8 to 12"' thick, up to 12 foot tall" | 2 | SDR | Costing for each 100 ft^2 Wall Panel | Superstructure | Masonry Wall
257 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 8 to 12"' thick, greater than 12 foot tall" | 2 | SDR | Costing for each 225 ft^2 Wall Panel | Superstructure | Masonry Wall
258 | Ordinary reinforced masonry walls with partially grouted cells, 8 to 12" thick, flexure dominated up to 12' tall" | 3 | SDR | Costing for each 100 ft^2 Wall Panel, | Superstructure | Masonry Wall
259 | Ordinary reinforced masonry walls with partially grouted cells, 8 to 12" thick, flexure dominated greater than 12' tall" | 3 | SDR | Costing for each 225 ft^2 Wall Panel | Superstructure | Masonry Wall
260 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 16 thick, up to 12 foot tall" | 2 | SDR | Costing for each 100 ft^2 Wall Panel | Superstructure | Masonry Wall
261 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated,16' thick, greater than 12 foot tall" | 2 | SDR | Costing for each 225 ft^2 Wall Panel | Superstructure | Masonry Wall
262 | Ordinary reinforced masonry walls with partially grouted cells, 16 thick, flexure dominated up to 12' tall" | 3 | SDR | Costing for each 100 ft^2 Wall Panel | Superstructure | Masonry Wall
263 | Ordinary reinforced masonry walls with partially grouted cells, 16 thick, flexure dominated greater than 12' tall" | 3 | SDR | Costing for each 225 ft^2 Wall Panel | Superstructure | Masonry Wall
264 | Special reinforced masonry walls with fully grouted cells, 8 or 12" thick, shear dominated, up t o12' tall" | 2 | SDR | Costing for each 100 ft^2 Wall Panel | Superstructure | Masonry Wall
265 | Special reinforced masonry walls with fully grouted cells, 8 or 12" thick, shear dominated, greater than 12' tall" | 2 | SDR | Costing for each 225 ft^2 Wall Panel | Superstructure | Masonry Wall
266 | Special reinforced masonry walls with fully grouted cells, 8 to 12" thick, flexure dominated up to 12' tall" | 3 | SDR | Costing for each 100 ft^2 Wall Panel | Superstructure | Masonry Wall
267 | Special reinforced masonry walls with fully grouted cells, 8 to 12" thick, flexure dominated greater than 12' tall" | 3 | SDR | Costing for each 225 ft^2 Wall Panel | Superstructure | Masonry Wall
268 | Special reinforced masonry walls with fully grouted cells, 16 thick, shear dominated, up to 12' tall" | 2 | SDR | Costing for each 100 ft^2 Wall Panel | Superstructure | Masonry Wall
269 | Special reinforced masonry walls with fully grouted cells, 16 thick, shear dominated, greater than 12' tall" | 2 | SDR | Costing for each 225 ft^2 Wall Panel | Superstructure | Masonry Wall
270 | Special reinforced masonry walls with fully grouted cells, 16 thick, flexure dominated up to 12' tall" | 3 | SDR | Costing for each 100 ft^2 Wall Panel | Superstructure | Masonry Wall
271 | Special reinforced masonry walls with fully grouted cells, 16 thick, flexure dominated greater than 12' tall" | 3 | SDR | Costing for each 225 ft^2 Wall Panel | Superstructure | Masonry Wall
272 | Cold formed steel walls with wood structural panel sheathing, interior - gypsum board | 3 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 38 mil cold formed steel framing with 7/16 OSB and 3/8 plywood panel sheathing with overturning restraint at each end of the wall per AISI design standard. No. 8 screws 2" to 6" OC at perimeter and 12" OC EW in field. | Superstructure | CFS Wall
273 | Cold formed steel walls with wood structural panel sheathing, exterior - stucco one side | 3 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 38 mil cold formed steel framing with 7/16 OSB and 3/8 plywood panel sheathing with overturning restraint at each end of the wall per AISI design standard. No. 8 screws 2" to 6" OC at perimeter and 12" OC EW in field. | Superstructure | CFS Wall
274 | Cold formed steel walls with flat strap X-bracing, interior - gypsum board | 2 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 33 mil cold formed steel framing with 4.5 inch x 33 mil flat strap X-bracing on one side. Straps attached to gussets with No. 8 screws. | Superstructure | CFS Wall
275 | Cold formed steel walls with flat strap X-bracing, exterior - stucco one side | 2 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 33 mil cold formed steel framing with 4.5 inch x 33 mil flat strap X-bracing on one side. Straps attached to gussets with No. 8 screws. | Superstructure | CFS Wall
276 | Cold formed steel walls with 22 or 31 mil steel sheathing, interior - gypsum board | 2 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 33 mil cold formed steel framing with 22 or 31 mil steel sheathing attached with No. 8 screws spaced 2" or 6" OC at perimeter and 12" OC EW in the field. | Superstructure | CFS Wall
277 | Cold formed steel walls with 22 or 31 mil steel sheathing, exterior - stucco one side | 2 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 33 mil cold formed steel framing with 22 or 31 mil steel sheathing attached with No. 8 screws spaced 2" or 6" OC at perimeter and 12" OC EW in the field. | Superstructure | CFS Wall
278 | Light framed wood walls with structural panel sheathing, gypsum wallboard no hold-downs | 3 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 1 SIDE: 3/8" OSB or 15/32 ply with 8d box nails at 4 to 6 inches along panel edges and 12 inches field nailing. DF #2, 2x4@16 studs. 1 SIDE: 1/2 gypsum board. Panel 8 feet tall, 8 or 16 feet long with or without door and window openings, double top plate, single bottom plate, no hold-downs. | Superstructure | Wood Wall
279 | Light framed wood walls with structural panel sheathing, stucco, hold-downs | 3 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 1 SIDE: 3/8" OSB or 15/32 ply with 8d box nails at 4 to 6 inches along panel edges and 12 inches field nailing. DF #2, 2x4@16 studs. 1 SIDE: 1/2 gypsum board. Panel 8 feet tall, 8 or 16 feet long with or without door and window openings, double top plate, single bottom plate, with hold-downs. Three layer 7/8" stucco with 1/2-inch chop strand fibers applied over wire mesh fastened with 1.25 -inch long staples. | Superstructure | Wood Wall
280 | Light framed wood walls with structural panel sheathing, stucco no hold-downs | 3 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 1 SIDE: 3/8" OSB or 15/32 ply with 8d box nails at 4 to 6 inches along panel edges and 12 inches field nailing. DF #2, 2x4@16 studs. 1 SIDE: 1/2 gypsum board. Panel 8 feet tall, 8 or 16 feet long with or without door and window openings, double top plate, single bottom plate, with no hold-downs. Three layer 7/8" stucco with 1/2-inch chop strand fibers applied over wire mesh fastened with 1.25 -inch long staples. | Superstructure | Wood Wall
281 | Light framed wood walls with structural panel sheathing, gypsum wallboard and hold-downs | 3 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 1 SIDE: 3/8" OSB or 15/32 ply with 8d box nails at 4 to 6 inches along panel edges and 12 inches field nailing. DF #2, 2x4@16 studs. 1 SIDE: 1/2 gypsum board. Panel 8 feet tall, 8 or 16 feet long with or without door and window openings, double top plate, single bottom plate, with hold-downs. | Superstructure | Wood Wall
282 | Wood walls with diagonal let-in bracing | 1 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: Stud wall framing consists of 2 x 4’s at 16 inches on center with double top plates and single sill plate. Diagonal bracing includes 2 forms. Block-bracing consists of diagonal blocking between studs that extends from the top of one edge of the panel to the bottom of the opposite edge. Diagonal bracing may also consist of let-in bracing for which a 1x or 2x brace (with same inclination as described for block-bracing) is recessed into studs. Walls may be sheathed with horizontal or vertical lumber siding. | Superstructure | Wood Wall
283 | Exterior Wall - Type: Gypsum with wood studs, Full Height, Fixed Below, Fixed Above | 3 | SDR | Costing based upon 13'x100' Panels | Exterior Enclosure | Exterior Wall
284 | Exterior Wall - Cold formed steel walls with wood structural panel sheathing, interior - gypsum board | 3 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 38 mil cold formed steel framing with 7/16 OSB and 3/8 plywood panel sheathing with overturning restraint at each end of the wall per AISI design standard. No. 8 screws 2" to 6" OC at perimeter and 12" OC EW in field. | Exterior Enclosure | Exterior Wall
285 | Exterior Wall - Cold formed steel walls with wood structural panel sheathing, exterior - stucco one side | 3 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 38 mil cold formed steel framing with 7/16 OSB and 3/8 plywood panel sheathing with overturning restraint at each end of the wall per AISI design standard. No. 8 screws 2" to 6" OC at perimeter and 12" OC EW in field. | Exterior Enclosure | Exterior Wall
286 | Exterior Wall - Cold formed steel walls with flat strap X-bracing, interior - gypsum board | 2 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 33 mil cold formed steel framing with 4.5 inch x 33 mil flat strap X-bracing on one side. Straps attached to gussets with No. 8 screws. | Exterior Enclosure | Exterior Wall
287 | Exterior Wall - Cold formed steel walls with flat strap X-bracing, exterior - stucco one side | 2 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 33 mil cold formed steel framing with 4.5 inch x 33 mil flat strap X-bracing on one side. Straps attached to gussets with No. 8 screws. | Exterior Enclosure | Exterior Wall
288 | Exterior Wall - Cold formed steel walls with 22 or 31 mil steel sheathing, interior - gypsum board | 2 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 33 mil cold formed steel framing with 22 or 31 mil steel sheathing attached with No. 8 screws spaced 2" or 6" OC at perimeter and 12" OC EW in the field. | Exterior Enclosure | Exterior Wall
289 | Exterior Wall - Cold formed steel walls with 22 or 31 mil steel sheathing, exterior - stucco one side | 2 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 33 mil cold formed steel framing with 22 or 31 mil steel sheathing attached with No. 8 screws spaced 2" or 6" OC at perimeter and 12" OC EW in the field. | Exterior Enclosure | Exterior Wall
290 | Exterior Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard no hold-downs | 3 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 1 SIDE: 3/8" OSB or 15/32 ply with 8d box nails at 4 to 6 inches along panel edges and 12 inches field nailing. DF #2, 2x4@16 studs. 1 SIDE: 1/2 gypsum board. Panel 8 feet tall, 8 or 16 feet long with or without door and window openings, double top plate, single bottom plate, no hold-downs. | Exterior Enclosure | Exterior Wall
291 | Exterior Wall - Light framed wood walls with structural panel sheathing, stucco, hold-downs | 3 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 1 SIDE: 3/8" OSB or 15/32 ply with 8d box nails at 4 to 6 inches along panel edges and 12 inches field nailing. DF #2, 2x4@16 studs. 1 SIDE: 1/2 gypsum board. Panel 8 feet tall, 8 or 16 feet long with or without door and window openings, double top plate, single bottom plate, with hold-downs. Three layer 7/8" stucco with 1/2-inch chop strand fibers applied over wire mesh fastened with 1.25 -inch long staples. | Exterior Enclosure | Exterior Wall
292 | Exterior Wall - Light framed wood walls with structural panel sheathing, stucco no hold-downs | 3 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 1 SIDE: 3/8" OSB or 15/32 ply with 8d box nails at 4 to 6 inches along panel edges and 12 inches field nailing. DF #2, 2x4@16 studs. 1 SIDE: 1/2 gypsum board. Panel 8 feet tall, 8 or 16 feet long with or without door and window openings, double top plate, single bottom plate, with no hold-downs. Three layer 7/8" stucco with 1/2-inch chop strand fibers applied over wire mesh fastened with 1.25 -inch long staples. | Exterior Enclosure | Exterior Wall
293 | Exterior Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard and hold-downs | 3 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: 1 SIDE: 3/8" OSB or 15/32 ply with 8d box nails at 4 to 6 inches along panel edges and 12 inches field nailing. DF #2, 2x4@16 studs. 1 SIDE: 1/2 gypsum board. Panel 8 feet tall, 8 or 16 feet long with or without door and window openings, double top plate, single bottom plate, with hold-downs. | Exterior Enclosure | Exterior Wall
294 | Exterior Wall - Wood walls with diagonal let-in bracing | 1 | SDR | Costing for each 100 ft^2 Wall Panel. Assumed framing: Stud wall framing consists of 2 x 4’s at 16 inches on center with double top plates and single sill plate. Diagonal bracing includes 2 forms. Block-bracing consists of diagonal blocking between studs that extends from the top of one edge of the panel to the bottom of the opposite edge. Diagonal bracing may also consist of let-in bracing for which a 1x or 2x brace (with same inclination as described for block-bracing) is recessed into studs. Walls may be sheathed with horizontal or vertical lumber siding. | Exterior Enclosure | Exterior Wall
295 | Precast Concrete Panels 4.5 inches thick - in plane deformation | 2 | SDR | Costing is based upon 30'x13' panels. | Exterior Enclosure | Concrete Panel
296 | Precast Concrete Panels 4.5 inches thick - out of plane deformation | 1 | PFA | Costing is based upon 30'x13' panels. | Exterior Enclosure | Concrete Panel
297 | Curtain Walls - Generic Midrise Stick-Built Curtain wall, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
298 | Curtain Walls - Generic Midrise Stick-Built Curtain wall, Config: Insulating Glass Units (dual pane), Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
299 | Midrise stick-built curtain wall, Config: Asymmetric insulating glass units (dual-pane, unequal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/2 in. (13 mm) outer AN LAM (0.030 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 3 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
300 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN LAM (0.030 PVB); glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
301 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN laminated, 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
302 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN laminated, 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
303 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
304 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0 in. (0 mm); aspect ratio = 6:5 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
305 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.13 in. (3 mm); aspect ratio = 6:5 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
306 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.25 in. (6 mm); aspect ratio = 6:5 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
307 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2:1 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
308 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1:2 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
309 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic, 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
310 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic, 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
311 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
312 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2:1 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
313 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1:2 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
314 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
315 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
316 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, Seamed Edge; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
317 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, Polished Edge; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
318 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Heat strengthened, Details: 1/4 in. (6 mm) HS monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
319 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/4 in. (6 mm) outer AN LAM (0.030 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 3 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
320 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/4 in. (6 mm) outer AN LAM (0.060 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 3 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
321 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN insulating glass unit (IGU) [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
322 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.25 in. (6 mm); aspect ratio = 6:5 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
323 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes], 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 3 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
324 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes], 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 3 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
325 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 3 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
326 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Heat strengthened, Details: 1 in. (25 mm) HS IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 3 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
327 | Curtain Walls - Unitized curtain wall (also generic unitized curtain wall), Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1-1/4 in. (32 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], 4-sided SSG, VHBTM SGTTM; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = Varies sealant = wet | 3 | SDR | Costing is based on 1 unit | Exterior Enclosure | Curtain Wall
328 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 3 | SDR | Costing is based on 1 unit | Exterior Enclosure | Glass Storefront
329 | Generic Storefront, Config: IGU, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 3 | SDR | Costing is based on 1 unit | Exterior Enclosure | Glass Storefront
330 | Storefront, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN LAM (0.030 PVB); glass-frame clearance = 0.41 in. (10 mm); aspect ratio = 6:5 sealant = dry | 3 | SDR | Costing is based on 1 unit | Exterior Enclosure | Glass Storefront
331 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.41 in. (10 mm); aspect ratio = 6:5 sealant = dry | 3 | SDR | Costing is based on 1 unit | Exterior Enclosure | Glass Storefront
332 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Planar Specimen; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 1.93:1 sealant = wet | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Glass Storefront
333 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Corner Cond. Specimen, in-plane; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 1.93:1 sealant = wet | 1 | SDR | Costing is based on 1 unit | Exterior Enclosure | Glass Storefront
334 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Corner Cond. Specimen, combined; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 1.93:1 sealant = wet | 1 | SDR | Costing is based on 1 unit | Exterior Enclosure | Glass Storefront
335 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Corner Cond. Specimen, Short side; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 2.72:1 sealant = wet | 1 | SDR | Costing is based on 1 unit | Exterior Enclosure | Glass Storefront
336 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU; glass-frame clearance = 0.59 in. (15 mm); aspect ratio = 6:5 sealant = dry | 3 | SDR | Costing is based on 1 unit | Exterior Enclosure | Glass Storefront
337 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Planar Specimen; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.89:1 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Glass Storefront
338 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, in-plane; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.89:1 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Glass Storefront
339 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, combined; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.89:1 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Glass Storefront
340 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, Short side; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2.83:1 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Glass Storefront
341 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Planar Specimen; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.88:1 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Glass Storefront
342 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, in-plane; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.88:1 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Glass Storefront
343 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, combined; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.88:1 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Glass Storefront
344 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, Short side; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2.82:1 sealant = dry | 2 | SDR | Costing is based on 1 unit | Exterior Enclosure | Glass Storefront
345 | Concrete tile roof, tiles secured and compliant with UBC94 | 2 | PFA | Costing per roofing square (100 SF) | Roofing | Concrete Tile Roof
346 | Clay tile roof, tiles secured and compliant with UBC94 | 2 | PFA | Costing per roofing square (100 SF) | Roofing | Clay Tile Roof
347 | Concrete tile roof, unsecured tiles | 2 | PFA | Costing per roofing square (100 SF) | Roofing | Concrete Tile Roof
348 | Clay tile roof, unsecured tiles | 2 | PFA | Costing per roofing square (100 SF) | Roofing | Clay Tile Roof
349 | Masonry Chimney - unreinforced, non industrial, above roof 5 ft, replace with masonry | 2 | PFA | Demand parameter shall be defined as the first floor peak floor acceleration. Unreinforced masonry chimney as a component of wood frame buildings. Includes firebox and chimney, excludes exterior veneer or ornamentation. May include chimneys where the quality of reinforcing is unknown. For multiple story buildings enter the chimney fragility once at the first floor, do not specify this fragility at subsequent elevated floors. | Roofing | Masonry Chimney
350 | Masonry Chimney - unreinforced, non industrial, above roof 10 ft, replace with masonry | 2 | PFA | Demand parameter shall be defined as the first floor peak floor acceleration. Unreinforced masonry chimney as a component of wood frame buildings. Includes firebox and chimney, excludes exterior veneer or ornamentation. May include chimneys where the quality of reinforcing is unknown. For multiple story buildings enter the chimney fragility once at the first floor, do not specify this fragility at subsequent elevated floors. | Roofing | Masonry Chimney
351 | Masonry Chimney - unreinforced, non industrial, above roof 15 ft, replace with masonry | 2 | PFA | Demand parameter shall be defined as the first floor peak floor acceleration. Unreinforced masonry chimney as a component of wood frame buildings. Includes firebox and chimney, excludes exterior veneer or ornamentation. May include chimneys where the quality of reinforcing is unknown. For multiple story buildings enter the chimney fragility once at the first floor, do not specify this fragility at subsequent elevated floors. | Roofing | Masonry Chimney
352 | Masonry Chimney - unreinforced, non industrial, above roof 5 ft, replace with framing | 2 | PFA | Demand parameter shall be defined as the first floor peak floor acceleration. Unreinforced masonry chimney as a component of wood frame buildings. Includes firebox and chimney, excludes exterior veneer or ornamentation. May include chimneys where the quality of reinforcing is unknown. For multiple story buildings enter the chimney fragility once at the first floor, do not specify this fragility at subsequent elevated floors. | Roofing | Masonry Chimney
353 | Masonry Chimney - unreinforced, non industrial, above roof 10 ft, replace with framing | 2 | PFA | Demand parameter shall be defined as the first floor peak floor acceleration. Unreinforced masonry chimney as a component of wood frame buildings. Includes firebox and chimney, excludes exterior veneer or ornamentation. May include chimneys where the quality of reinforcing is unknown. For multiple story buildings enter the chimney fragility once at the first floor, do not specify this fragility at subsequent elevated floors. | Roofing | Masonry Chimney
354 | Masonry Chimney - unreinforced, non industrial, above roof 15 ft, replace with framing | 2 | PFA | Demand parameter shall be defined as the first floor peak floor acceleration. Unreinforced masonry chimney as a component of wood frame buildings. Includes firebox and chimney, excludes exterior veneer or ornamentation. May include chimneys where the quality of reinforcing is unknown. For multiple story buildings enter the chimney fragility once at the first floor, do not specify this fragility at subsequent elevated floors. | Roofing | Masonry Chimney
355 | Masonry Parapet - unreinforced, unbraced | 2 | PFA | Unreinforced and unbraced masonry parapet as a component of a masonry building. Parapet height / width of approximately 3. Costing based upon repair of 3ft tall x 10ft segment. | Roofing | Masonry Parapet
356 | Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Fixed Above | 3 | SDR | Quantity is based upon 13'x100' Panels. Quantity of wall damaged varies by damage state. | Interiors | Wall Partition
357 | Wall Partition, Type: Gypsum with metal studs, Partial Height, Fixed Below, Lateral Braced Above | 3 | SDR | Quantity is based upon 13'x100' Panels. Quantity of wall damaged varies by damage state. | Interiors | Wall Partition
358 | Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Slip Track Above with returns | 3 | SDR | Quantity is based upon 13'x100' Panels. Quantity of wall damaged varies by damage state. | Interiors | Wall Partition
359 | Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Slip Track Above w/o returns (friction connections) | 2 | SDR | Quantity is based upon 13'x100' Panels. Quantity of wall damaged varies by damage state. | Interiors | Wall Partition
360 | Wall Partition, Type: Gypsum with wood studs, Full Height, Fixed Below, Fixed Above | 3 | SDR | Quantity is based upon 13'x100' Panels. Quantity of wall damaged varies by damage state. | Interiors | Wall Partition
361 | Prefabricated steel stair with steel treads and landings with seismic joints that accommodate drift. | 3 | SDR | Flexible stair with seismic interstory slip joint. Steel prefab stringers, steel or concrete filled pan treads. | Interiors | Steel Stairs
362 | Prefabricated steel stair with steel treads and landings with no seismic joint. | 3 | SDR | Flexible stair without seismic interstory slip joint. Steel prefab stringers, steel or concrete filled pan treads. | Interiors | Steel Stairs
363 | Non-monolithic precast concrete stair assembly with concrete stringers and treads with seismic joints that accommodate drift. | 3 | SDR | Rigid stair with seismic interstory drift joint. Precast concrete stair. | Interiors | Precast Stairs
364 | Non-monolithic precast concrete stair assembly with concrete stringers and treads with no seismic joint. | 3 | SDR | Rigid stair without seismic interstory drift joint. Precast concrete stair. | Interiors | Precast Stairs
365 | Monolithic cast-in-place and precast concrete stairs with seismic joints that accommodate drift - replace in kind if replacement is required. | 3 | SDR | Cast in place concrete stair, with seismic interstory drift joint | Interiors | Precast Stairs
366 | Monolithic cast-in-place and precast concrete stairs with no seismic joints - replace in kind if replacement is required. | 3 | SDR | Cast in place concrete stair, no seismic interstory drift joint | Interiors | Precast Stairs
367 | Monolithic cast-in-place and precast concrete stairs with seismic joints that accommodate drift - replace with prefabricated steel stair if replacement is required. | 3 | SDR | Cast in place concrete stair, with seismic interstory drift joint | Interiors | Precast Stairs
368 | Monolithic cast-in-place and precast concrete stairs with no seismic joints - replace with prefabricated steel stair if replacement is required. | 3 | SDR | Cast in place concrete stair, no seismic interstory drift joint | Interiors | Precast Stairs
369 | Hybrid stair assembly with steel stringers and concrete treads and landings with seismic joints that accommodate drift. | 3 | SDR | Stair consists of steel stringers with precast treads rigidly linked to stringer | Interiors | Stair Assembly
370 | Hybrid stair assembly with steel stringers and concrete treads and landings with no seismic joints. | 3 | SDR | Stair consists of steel stringers with precast treads rigidly linked to stringer | Interiors | Stair Assembly
371 | Wall Partition, Type: Gypsum + Wallpaper, Full Height, Fixed Below, Fixed Above | 1 | SDR | Costing based upon 9'x100' Panels | Interiors | Wall Partition
372 | Wall Partition, Type: Gypsum + Wallpaper, Partial Height, Fixed Below, Lateral Braced Above | 1 | SDR | Costing based upon 9'x100' Panels | Interiors | Wall Partition
373 | Wall Partition, Type: Gypsum + Wallpaper, Full Height, Fixed Below, Slip Track Above w/ returns (friction connection) | 1 | SDR | Costing based upon 9'x100' Panels | Interiors | Wall Partition
374 | Wall Partition, Type: Gypsum + Wallpaper, Full Height, Fixed Below, Slip Track Above w/o returns (friction connection) | 1 | SDR | Costing based upon 9'x100' Panels | Interiors | Wall Partition
375 | Wall Partition, Type: Gypsum + Ceramic Tile, Full Height, Fixed Below, Fixed Above | 2 | SDR | Costing based upon 9'x100' Panels | Interiors | Wall Partition
376 | Wall Partition, Type: Gypsum + Ceramic Tile, Partial Height, Fixed Below, Lateral Braced Above | 2 | SDR | Costing based upon 9'x100' Panels | Interiors | Wall Partition
377 | Wall Partition, Type: Gypsum + Ceramic Tile, Full Height, Fixed Below, Slip Track Above w/ returns (friction connection) | 2 | SDR | Costing based upon 9'x100' Panels | Interiors | Wall Partition
378 | Wall Partition, Type: Gypsum + Ceramic Tile, Full Height, Fixed Below, Slip Track Above w/o returns (friction connection) | 2 | SDR | Costing based upon 9'x100' Panels | Interiors | Wall Partition
379 | Wall Partition, Type: High End Marble or Wood Panel, Full Height, Fixed Below, Fixed Above | 2 | SDR | Costing based upon 9'x100' Panels | Interiors | Wall Partition
380 | Wall Partition, Type: High End Marble or Wood Panel, Partial Height, Fixed Below, Lateral Braced Above | 2 | SDR | Costing based upon 9'x100' Panels | Interiors | Wall Partition
381 | Wall Partition, Type: High End Marble or Wood Panel, Full Height, Fixed Below, Slip Track Above w/ returns (friction connection) | 2 | SDR | Costing based upon 9'x100' Panels | Interiors | Wall Partition
382 | Wall Partition, Type: High End Marble or Wood Panel, Full Height, Fixed Below, Slip Track Above w/o returns (friction connection) | 2 | SDR | Costing based upon 9'x100' Panels | Interiors | Wall Partition
383 | Generic Floor Covering - Flooding of floor caused by failure of pipe - Office - Dry | 1 | PFA | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be carpet or vinyl. Available costs are per one square foot of floor area. | Interiors | Floor Covering
384 | Generic Floor Covering - Flooding of floor caused by failure of pipe - Office - Humid | 1 | PFA | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be carpet or vinyl. Available costs are per one square foot of floor area. | Interiors | Floor Covering
385 | Generic Floor Covering - Flooding of floor caused by failure of pipe - Laboratory - Dry | 1 | PFA | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be sheet vinyl. Available costs are per one square foot of floor area. | Interiors | Floor Covering
386 | Generic Floor Covering - Flooding of floor caused by failure of pipe - Laboratory - Humid | 1 | PFA | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be sheet vinyl. Available costs are per one square foot of floor area. | Interiors | Floor Covering
387 | Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospital - Dry | 1 | PFA | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be sheet vinyl. Available costs are per one square foot of floor area. | Interiors | Floor Covering
388 | Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospital - Humid | 1 | PFA | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be sheet vinyl. Available costs are per one square foot of floor area. | Interiors | Floor Covering
389 | Generic Floor Covering - Flooding of floor caused by failure of pipe - School - Dry | 1 | PFA | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be vinyl composition tile. Available costs are per one square foot of floor area. | Interiors | Floor Covering
390 | Generic Floor Covering - Flooding of floor caused by failure of pipe - School - Humid | 1 | PFA | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be vinyl composition tile. Available costs are per one square foot of floor area. | Interiors | Floor Covering
391 | Generic Floor Covering - Flooding of floor caused by failure of pipe - Apartments - Dry | 1 | PFA | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be carpet. Available costs are per one square foot of floor area. | Interiors | Floor Covering
392 | Generic Floor Covering - Flooding of floor caused by failure of pipe - Apartments - Humid | 1 | PFA | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be carpet. Available costs are per one square foot of floor area. | Interiors | Floor Covering
393 | Generic Floor Covering - Flooding of floor caused by failure of pipe - Retail - Dry | 1 | PFA | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be vinyl composition tile. Available costs are per one square foot of floor area. | Interiors | Floor Covering
394 | Generic Floor Covering - Flooding of floor caused by failure of pipe - Retail - Humid | 1 | PFA | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be vinyl composition tile. Available costs are per one square foot of floor area. | Interiors | Floor Covering
395 | Generic Floor Covering - Flooding of floor caused by failure of pipe - Warehouse - Dry | 1 | PFA | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be sealed concrete. Available costs are per one square foot of floor area. | Interiors | Floor Covering
396 | Generic Floor Covering - Flooding of floor caused by failure of pipe - Warehouse - Humid | 1 | PFA | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be sealed concrete. Available costs are per one square foot of floor area. | Interiors | Floor Covering
397 | Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospitality - Dry | 1 | PFA | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be carpet. Available costs are per one square foot of floor area. | Interiors | Floor Covering
398 | Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospitality - Humid | 1 | PFA | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be carpet. Available costs are per one square foot of floor area. | Interiors | Floor Covering
399 | Raised Access Floor, non seismically rated. | 1 | PFA | Access floor unanchored or anchored with adhesive. Costing is based upon a xxx SF floor area. | Interiors | Raised Access Floor
400 | Raised Access Floor, seismically rated. | 1 | PFA | Access floor is designed to meet code requirements and mechanically anchored and braced as necessary to resist anchor loads. Equipment is anchored to floor systems and heavier equipment is anchored directly to the structural floor. Costing is based upon a xxx SF floor area. | Interiors | Raised Access Floor
401 | Suspended Ceiling, SDC A,B,C, Area (A): A < 250, Vert support only | 3 | PFA | Costing for each 250 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wires only. Includes lighting fixtures in suspended ceiling. | Interiors | Suspended Ceiling
402 | Suspended Ceiling, SDC A,B,C, Area (A): 250 < A < 1000, Vert support only | 3 | PFA | Costing for each 600 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wires only. Includes lighting fixtures in suspended ceiling. | Interiors | Suspended Ceiling
403 | Suspended Ceiling, SDC A,B,C, Area (A): 1000 < A < 2500, Vert support only | 3 | PFA | Costing for each 1800 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wires only. Includes lighting fixtures in suspended ceiling. | Interiors | Suspended Ceiling
404 | Suspended Ceiling, SDC A,B,C, Area (A): A > 2500, Vert support only | 3 | PFA | Costing for each 2500 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wires only. Includes lighting fixtures in suspended ceiling. | Interiors | Suspended Ceiling
405 | Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): A < 250, Vert & Lat support | 3 | PFA | Costing for each 250 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wire, diagonal wires, and compression posts, 2 inch wide ledger support angles at wall and oversize holes around tile openings. Includes lighting fixtures in suspended ceiling. | Interiors | Suspended Ceiling
406 | Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): 250 < A < 1000, Vert & Lat support | 3 | PFA | Costing for each 600 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wire, diagonal wires, and compression posts, 2 inch wide ledger support angles at wall and oversize holes around tile openings. Includes lighting fixtures in suspended ceiling. | Interiors | Suspended Ceiling
407 | Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): 1000 < A < 2500, Vert & Lat support | 3 | PFA | Costing for each 1800 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wire, diagonal wires, and compression posts, 2 inch wide ledger support angles at wall and oversize holes around tile openings. Includes lighting fixtures in suspended ceiling. | Interiors | Suspended Ceiling
408 | Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): A > 2500, Vert & Lat support | 3 | PFA | Costing for each 2500 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wire, diagonal wires, and compression posts, 2 inch wide ledger support angles at wall and oversize holes around tile openings. Includes lighting fixtures in suspended ceiling. | Interiors | Suspended Ceiling
409 | Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): A < 250, Vert & Lat support | 3 | PFA | Costing for each 250 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wire, diagonal wires, and compression posts, 2 inch wide ledger support angles at wall and oversize holes around tile openings. Includes lighting fixtures in suspended ceiling. | Interiors | Suspended Ceiling
410 | Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): 250 < A < 1000, Vert & Lat support | 3 | PFA | Costing for each 600 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wire, diagonal wires, and compression posts, 2 inch wide ledger support angles at wall and oversize holes around tile openings. Includes lighting fixtures in suspended ceiling. | Interiors | Suspended Ceiling
411 | Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): 1000 < A < 2500, Vert & Lat support | 3 | PFA | Costing for each 1800 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wire, diagonal wires, and compression posts, 2 inch wide ledger support angles at wall and oversize holes around tile openings. Includes lighting fixtures in suspended ceiling. | Interiors | Suspended Ceiling
412 | Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): A > 2500, Vert & Lat support | 3 | PFA | Costing for each 2500 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wire, diagonal wires, and compression posts, 2 inch wide ledger support angles at wall and oversize holes around tile openings. Includes lighting fixtures in suspended ceiling. | Interiors | Suspended Ceiling
413 | Independent Pendant Lighting - non seismic | 1 | PFA | Horizontal light fixtures 4 to 16 ft long suspended 12 to 24 inches from ceiling. No seismic design or bracing. Hung from ceiling above by two or more rods or cables. | Interiors | Pendant Lighting
414 | Independent Pendant Lighting - seismically rated | 1 | PFA | Horizontal light fixtures 4 to 16 ft long suspended 12 to 24 inches from ceiling. Hung from ceiling above by two or more rods or cables. Fixture and rods or cables are either designed for seismic movements or are laterally braced to prevent sway. | Interiors | Pendant Lighting
415 | Traction Elevator – Applies to most California Installations 1976 or later, most western states installations 1982 or later and most other U.S installations 1998 or later. | 4 | PGA | Costing per elevator. Elevator demand parameter shall be defined as the peak floor acceleration at the first floor. The elevator fragility for a multiple story building should only be entered once on the first floor. | Conveying | Traction Elevator
416 | Traction Elevator – Applies to most California Installations prior to 1976, most western states installations prior to 1982 and most other U.S installations prior to 1998. | 4 | PGA | Costing per elevator. Elevator demand parameter shall be defined as the peak floor acceleration at the first floor. The elevator fragility for a multiple story building should only be entered once on the first floor. | Conveying | Traction Elevator
417 | Hydraulic Elevator – Applies to most California Installations 1976 or later, most western states installations postdating 1982 and most U.S installations postdating 1998. | 4 | PGA | Costing per elevator. Elevator demand parameter shall be defined as the peak floor acceleration at the first floor. The elevator fragility for a multiple story building should only be entered once on the first floor. | Conveying | Hydraulic Elevator
418 | Hydraulic Elevator – Applies to most California Installations prior to 1976, most western states installations prior to 1982 and most U.S installations prior to 1998. | 4 | PGA | Costing per elevator. Elevator demand parameter shall be defined as the peak floor acceleration at the first floor. The elevator fragility for a multiple story building should only be entered once on the first floor. | Conveying | Hydraulic Elevator
419 | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Plumbing | Steam Piping
420 | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, BRACING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Plumbing | Steam Piping
421 | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Plumbing | Steam Piping
422 | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Plumbing | Steam Piping
423 | Chiller - Capacity: < 100 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 75 Ton. | HAVC | Chiller
424 | Chiller - Capacity: 100 to <350 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 250 Ton. | HAVC | Chiller
425 | Chiller - Capacity: 350 to <750 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 500 Ton. | HAVC | Chiller
426 | Chiller - Capacity: 750 to <1000 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 850 Ton. | HAVC | Chiller
427 | Chiller - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 75 Ton. | HAVC | Chiller
428 | Chiller - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 75 Ton. | HAVC | Chiller
429 | Chiller - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 75 Ton. | HAVC | Chiller
430 | Chiller - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 250 Ton. | HAVC | Chiller
431 | Chiller - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 250 Ton. | HAVC | Chiller
432 | Chiller - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 250 Ton. | HAVC | Chiller
433 | Chiller - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 500 Ton. | HAVC | Chiller
434 | Chiller - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 500 Ton. | HAVC | Chiller
435 | Chiller - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 500 Ton. | HAVC | Chiller
436 | Chiller - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 850 Ton. | HAVC | Chiller
437 | Chiller - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 850 Ton. | HAVC | Chiller
438 | Chiller - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 850 Ton. | HAVC | Chiller
439 | Chiller - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 75 Ton. | HAVC | Chiller
440 | Chiller - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 75 Ton. | HAVC | Chiller
441 | Chiller - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 75 Ton. | HAVC | Chiller
442 | Chiller - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 250 Ton. | HAVC | Chiller
443 | Chiller - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 250 Ton. | HAVC | Chiller
444 | Chiller - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 250 Ton. | HAVC | Chiller
445 | Chiller - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 500 Ton. | HAVC | Chiller
446 | Chiller - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 500 Ton. | HAVC | Chiller
447 | Chiller - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 500 Ton. | HAVC | Chiller
448 | Chiller - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 850 Ton. | HAVC | Chiller
449 | Chiller - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 850 Ton. | HAVC | Chiller
450 | Chiller - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 850 Ton. | HAVC | Chiller
451 | Cooling Tower - Capacity: < 100 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 75 Ton. | HAVC | Cooling Tower
452 | Cooling Tower - Capacity: 100 to <350 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 250 Ton. | HAVC | Cooling Tower
453 | Cooling Tower - Capacity: 350 to <750 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 500 Ton. | HAVC | Cooling Tower
454 | Cooling Tower - Capacity: 750 to <1000 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 850 Ton. | HAVC | Cooling Tower
455 | Cooling Tower - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 75 Ton. | HAVC | Cooling Tower
456 | Cooling Tower - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 75 Ton. | HAVC | Cooling Tower
457 | Cooling Tower - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 75 Ton. | HAVC | Cooling Tower
458 | Cooling Tower - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 250 Ton. | HAVC | Cooling Tower
459 | Cooling Tower - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 250 Ton. | HAVC | Cooling Tower
460 | Cooling Tower - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 250 Ton. | HAVC | Cooling Tower
461 | Cooling Tower - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 500 Ton. | HAVC | Cooling Tower
462 | Cooling Tower - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 500 Ton. | HAVC | Cooling Tower
463 | Cooling Tower - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 500 Ton. | HAVC | Cooling Tower
464 | Cooling Tower - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 850 Ton. | HAVC | Cooling Tower
465 | Cooling Tower - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 850 Ton. | HAVC | Cooling Tower
466 | Cooling Tower - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 850 Ton. | HAVC | Cooling Tower
467 | Cooling Tower - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 75 Ton. | HAVC | Cooling Tower
468 | Cooling Tower - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 75 Ton. | HAVC | Cooling Tower
469 | Cooling Tower - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 75 Ton. | HAVC | Cooling Tower
470 | Cooling Tower - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 250 Ton. | HAVC | Cooling Tower
471 | Cooling Tower - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 250 Ton. | HAVC | Cooling Tower
472 | Cooling Tower - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 250 Ton. | HAVC | Cooling Tower
473 | Cooling Tower - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 500 Ton. | HAVC | Cooling Tower
474 | Cooling Tower - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 500 Ton. | HAVC | Cooling Tower
475 | Cooling Tower - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 500 Ton. | HAVC | Cooling Tower
476 | Cooling Tower - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 850 Ton. | HAVC | Cooling Tower
477 | Cooling Tower - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 850 Ton. | HAVC | Cooling Tower
478 | Cooling Tower - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 850 Ton. | HAVC | Cooling Tower
479 | Compressor - Capacity: Small non medical air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
480 | Compressor - Capacity: Large non medical air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
481 | Compressor - Capacity: Small medical quality air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
482 | Compressor - Capacity: Large medical quality air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
483 | Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
484 | Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
485 | Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 4 | PFA | Costing is per unit. | HAVC | Compressor
486 | Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
487 | Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
488 | Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 4 | PFA | Costing is per unit. | HAVC | Compressor
489 | Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
490 | Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
491 | Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 4 | PFA | Costing is per unit. | HAVC | Compressor
492 | Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
493 | Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
494 | Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 4 | PFA | Costing is per unit. | HAVC | Compressor
495 | Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
496 | Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
497 | Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 4 | PFA | Costing is per unit. | HAVC | Compressor
498 | Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
499 | Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
500 | Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 4 | PFA | Costing is per unit. | HAVC | Compressor
501 | Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
502 | Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
503 | Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 4 | PFA | Costing is per unit. | HAVC | Compressor
504 | Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
505 | Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 2 | PFA | Costing is per unit. | HAVC | Compressor
506 | Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 4 | PFA | Costing is per unit. | HAVC | Compressor
507 | HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC A or B | 2 | PFA | Costing per 10 units | HAVC | HVAC Fan
508 | HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC C | 2 | PFA | Costing per 10 units | HAVC | HVAC Fan
509 | HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC D, E, F | 2 | PFA | Costing per 10 units | HAVC | HVAC Fan
510 | HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC D, E, F (OSHPD or sim) | 2 | PFA | Costing per 10 units | HAVC | HVAC Fan
511 | HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC A or B | 1 | PFA | Costing per 10 units | HAVC | HVAC Fan
512 | HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC C | 1 | PFA | Costing per 10 units | HAVC | HVAC Fan
513 | HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC D, E, F | 1 | PFA | Costing per 10 units | HAVC | HVAC Fan
514 | HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC D, E, F (OSHPD or sim) | 1 | PFA | Costing per 10 units | HAVC | HVAC Fan
515 | HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC A or B | 2 | PFA | Costing based upon 1000 ft segments of duct | HAVC | HVAC Ducting
516 | HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC C | 2 | PFA | Costing based upon 1000 ft segments of duct | HAVC | HVAC Ducting
517 | HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F | 2 | PFA | Costing based upon 1000 ft segments of duct | HAVC | HVAC Ducting
518 | HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F (OSHPD or sim) | 2 | PFA | Costing based upon 1000 ft segments of duct | HAVC | HVAC Ducting
519 | HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC A or B | 2 | PFA | Costing based upon 1000 ft segments of duct | HAVC | HVAC Ducting
520 | HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC C | 2 | PFA | Costing based upon 1000 ft segments of duct | HAVC | HVAC Ducting
521 | HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F | 2 | PFA | Costing based upon 1000 ft segments of duct | HAVC | HVAC Ducting
522 | HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F (OSHPD or sim) | 2 | PFA | Costing based upon 1000 ft segments of duct | HAVC | HVAC Ducting
523 | HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC A or B | 2 | PFA | Costing based upon 1000 ft segments of duct | HAVC | HVAC Ducting
524 | HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC C | 2 | PFA | Costing based upon 1000 ft segments of duct | HAVC | HVAC Ducting
525 | HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F | 2 | PFA | Costing based upon 1000 ft segments of duct | HAVC | HVAC Ducting
526 | HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F (OSHPD or sim) | 2 | PFA | Costing based upon 1000 ft segments of duct | HAVC | HVAC Ducting
527 | HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC A or B | 2 | PFA | Costing based upon 1000 ft segments of duct | HAVC | HVAC Ducting
528 | HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC C | 2 | PFA | Costing based upon 1000 ft segments of duct | HAVC | HVAC Ducting
529 | HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F | 2 | PFA | Costing based upon 1000 ft segments of duct | HAVC | HVAC Ducting
530 | HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F (OSHPD or sim) | 2 | PFA | Costing based upon 1000 ft segments of duct | HAVC | HVAC Ducting
531 | HVAC Drops / Diffusers in suspended ceilings - No independent safety wires, SDC A or B | 1 | PFA | Costing per 10 units, No independent safety wires | HAVC | HVAC Drops/Diffusers
532 | HVAC Drops / Diffusers in suspended ceilings - No independent safety wires, SDC C | 1 | PFA | Costing per 10 units, No independent safety wires | HAVC | HVAC Drops/Diffusers
533 | HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC A or B | 1 | PFA | Costing per 10 units, unit supported by ducting only, no independent safety wires | HAVC | HVAC Drops/Diffusers
534 | HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC C | 1 | PFA | Costing per 10 units, unit supported by ducting only, no independent safety wires | HAVC | HVAC Drops/Diffusers
535 | HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC D, E, or F | 1 | PFA | Costing per 10 units, unit supported by ducting only, no independent safety wires | HAVC | HVAC Drops/Diffusers
536 | HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC D, E, or F (OSHPD or sim) | 1 | PFA | Costing per 10 units, unit supported by ducting only, no independent safety wires | HAVC | HVAC Drops/Diffusers
537 | Variable Air Volume (VAV) box with in-line coil, SDC A or B | 1 | PFA | Costing per 10 units | HAVC | Variable Air Volume
538 | Variable Air Volume (VAV) box with in-line coil, SDC C | 1 | PFA | Costing per 10 units | HAVC | Variable Air Volume
539 | HVAC Fan - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit. | HAVC | HVAC Fan
540 | HVAC Fan - Capacity: all - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 2 | PFA | Costing is per unit. | HAVC | HVAC Fan
541 | HVAC Fan - Capacity: all - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 1 | PFA | Costing is per unit. | HAVC | HVAC Fan
542 | HVAC Fan - Capacity: all - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit. | HAVC | HVAC Fan
543 | HVAC Fan - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit. | HAVC | HVAC Fan
544 | HVAC Fan - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit. | HAVC | HVAC Fan
545 | HVAC Fan - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit. | HAVC | HVAC Fan
546 | Air Handling Unit - Capacity: <5000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only | 2 | PFA | Costing is per unit and is based upon 4000 CFM. | HAVC | Air Handling Unit
547 | Air Handling Unit - Capacity: 5000 to <10000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only | 2 | PFA | Costing is per unit and is based upon 8000 CFM. | HAVC | Air Handling Unit
548 | Air Handling Unit - Capacity: 10000 to <25000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only | 2 | PFA | Costing is per unit and is based upon 20000 CFM. | HAVC | Air Handling Unit
549 | Air Handling Unit - Capacity: 25000 to <40000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only | 2 | PFA | Costing is per unit and is based upon 30000 CFM. | HAVC | Air Handling Unit
550 | Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 4000 CFM. | HAVC | Air Handling Unit
551 | Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 2 | PFA | Costing is per unit and is based upon 4000 CFM. | HAVC | Air Handling Unit
552 | Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 4 | PFA | Costing is per unit and is based upon 4000 CFM. | HAVC | Air Handling Unit
553 | Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 8000 CFM. | HAVC | Air Handling Unit
554 | Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 2 | PFA | Costing is per unit and is based upon 8000 CFM. | HAVC | Air Handling Unit
555 | Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 4 | PFA | Costing is per unit and is based upon 8000 CFM. | HAVC | Air Handling Unit
556 | Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 20000 CFM. | HAVC | Air Handling Unit
557 | Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 2 | PFA | Costing is per unit and is based upon 20000 CFM. | HAVC | Air Handling Unit
558 | Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 4 | PFA | Costing is per unit and is based upon 20000 CFM. | HAVC | Air Handling Unit
559 | Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 30000 CFM. | HAVC | Air Handling Unit
560 | Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 2 | PFA | Costing is per unit and is based upon 30000 CFM. | HAVC | Air Handling Unit
561 | Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 4 | PFA | Costing is per unit and is based upon 30000 CFM. | HAVC | Air Handling Unit
562 | Control Panel - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit. | HAVC | Control Panel
563 | Control Panel - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit. | HAVC | Control Panel
564 | Control Panel - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit. | HAVC | Control Panel
565 | Control Panel - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit. | HAVC | Control Panel
566 | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC A or B, PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, horizontal main and branches | Fire Protection | Fire Sprinkler
567 | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC C, PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, horizontal main and branches | Fire Protection | Fire Sprinkler
568 | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - Poorly designed bracing, SDC D, E, or F , PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, horizontal main and branches | Fire Protection | Fire Sprinkler
569 | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - with designed bracing, SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, horizontal main and branches | Fire Protection | Fire Sprinkler
570 | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC A or B | 2 | PFA | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Fire Protection | Fire Sprinkler
571 | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC C | 2 | PFA | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Fire Protection | Fire Sprinkler
572 | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F | 1 | PFA | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Fire Protection | Fire Sprinkler
573 | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) | 1 | PFA | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Fire Protection | Fire Sprinkler
574 | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC A or B | 2 | PFA | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Fire Protection | Fire Sprinkler
575 | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC C | 2 | PFA | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Fire Protection | Fire Sprinkler
576 | Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F | 2 | PFA | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Fire Protection | Fire Sprinkler
577 | Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) | 2 | PFA | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Fire Protection | Fire Sprinkler
578 | Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC D, E, or F | 2 | PFA | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Fire Protection | Fire Sprinkler
579 | Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) | 2 | PFA | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Fire Protection | Fire Sprinkler
580 | Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC A or B | 2 | PFA | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Fire Protection | Fire Sprinkler
581 | Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC C | 2 | PFA | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Fire Protection | Fire Sprinkler
582 | Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC D, E, or F | 2 | PFA | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Fire Protection | Fire Sprinkler
583 | Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) | 2 | PFA | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Fire Protection | Fire Sprinkler
584 | Transformer/primary service - Capacity: <100 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 75 kVa. | Electrical | Transformer/Primary Service
585 | Transformer/primary service - Capacity: 100 to <350 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 250 kVa. | Electrical | Transformer/Primary Service
586 | Transformer/primary service - Capacity: 350 to <750 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 500 kVa. | Electrical | Transformer/Primary Service
587 | Transformer/primary service - Capacity: 750 to 1500 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 1000 kVa. | Electrical | Transformer/Primary Service
588 | Transformer/primary service - Capacity: <100 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 75 kVa. | Electrical | Transformer/Primary Service
589 | Transformer/primary service - Capacity: <100 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 75 kVa. | Electrical | Transformer/Primary Service
590 | Transformer/primary service - Capacity: <100 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 75 kVa. | Electrical | Transformer/Primary Service
591 | Transformer/primary service - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 250 kVa. | Electrical | Transformer/Primary Service
592 | Transformer/primary service - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 250 kVa. | Electrical | Transformer/Primary Service
593 | Transformer/primary service - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 250 kVa. | Electrical | Transformer/Primary Service
594 | Transformer/primary service - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 500 kVa. | Electrical | Transformer/Primary Service
595 | Transformer/primary service - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 500 kVa. | Electrical | Transformer/Primary Service
596 | Transformer/primary service - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 500 kVa. | Electrical | Transformer/Primary Service
597 | Transformer/primary service - Capacity: 750 to 1500 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 1000 kVa. | Electrical | Transformer/Primary Service
598 | Transformer/primary service - Capacity: 750 to 1500 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 1000 kVa. | Electrical | Transformer/Primary Service
599 | Transformer/primary service - Capacity: 750 to 1500 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 1000 kVa. | Electrical | Transformer/Primary Service
600 | Motor Control Center - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit. | Electrical | Motor Control Center
601 | Motor Control Center - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit. | Electrical | Motor Control Center
602 | Motor Control Center - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit. | Electrical | Motor Control Center
603 | Motor Control Center - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit. | Electrical | Motor Control Center
604 | Low Voltage Switchgear - Capacity: 100 to <350 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 225 Amp. | Electrical | Low Voltage Switchgear
605 | Low Voltage Switchgear - Capacity: 350 to <750 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 400 Amp. | Electrical | Low Voltage Switchgear
606 | Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 800 Amp. | Electrical | Low Voltage Switchgear
607 | Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 1600 Amp. | Electrical | Low Voltage Switchgear
608 | Low Voltage Switchgear - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 225 Amp. | Electrical | Low Voltage Switchgear
609 | Low Voltage Switchgear - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 225 Amp. | Electrical | Low Voltage Switchgear
610 | Low Voltage Switchgear - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 225 Amp. | Electrical | Low Voltage Switchgear
611 | Low Voltage Switchgear - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 400 Amp. | Electrical | Low Voltage Switchgear
612 | Low Voltage Switchgear - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 400 Amp. | Electrical | Low Voltage Switchgear
613 | Low Voltage Switchgear - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 400 Amp. | Electrical | Low Voltage Switchgear
614 | Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 800 Amp. | Electrical | Low Voltage Switchgear
615 | Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 800 Amp. | Electrical | Low Voltage Switchgear
616 | Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 800 Amp. | Electrical | Low Voltage Switchgear
617 | Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 1600 Amp. | Electrical | Low Voltage Switchgear
618 | Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 1600 Amp. | Electrical | Low Voltage Switchgear
619 | Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 1600 Amp. | Electrical | Low Voltage Switchgear
620 | Distribution Panel - Capacity: 100 to <350 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 225 Amp. | Electrical | Distribution Panel
621 | Distribution Panel - Capacity: 350 to <750 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 400 Amp. | Electrical | Distribution Panel
622 | Distribution Panel - Capacity: 750 to <1200 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 800 Amp. | Electrical | Distribution Panel
623 | Distribution Panel - Capacity: 1200 to 2000 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 1600 Amp. | Electrical | Distribution Panel
624 | Distribution Panel - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 225 Amp. | Electrical | Distribution Panel
625 | Distribution Panel - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 225 Amp. | Electrical | Distribution Panel
626 | Distribution Panel - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 225 Amp. | Electrical | Distribution Panel
627 | Distribution Panel - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 400 Amp. | Electrical | Distribution Panel
628 | Distribution Panel - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 400 Amp. | Electrical | Distribution Panel
629 | Distribution Panel - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 400 Amp. | Electrical | Distribution Panel
630 | Distribution Panel - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 800 Amp. | Electrical | Distribution Panel
631 | Distribution Panel - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 800 Amp. | Electrical | Distribution Panel
632 | Distribution Panel - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 800 Amp. | Electrical | Distribution Panel
633 | Distribution Panel - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 1600 Amp. | Electrical | Distribution Panel
634 | Distribution Panel - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1 | PFA | Costing is per unit and is based upon 1600 Amp. | Electrical | Distribution Panel
635 | Distribution Panel - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 3 | PFA | Costing is per unit and is based upon 1600 Amp. | Electrical | Distribution Panel
636 | Battery Rack - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | 3 | PFA | Costing is per unit. | Electrical | Battery Rack
637 | Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit. | Electrical | Battery Rack
638 | Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 3 | PFA | Costing is per unit. | Electrical | Battery Rack
639 | Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 5 | PFA | Costing is per unit. | Electrical | Battery Rack
640 | Battery Charger - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | 2 | PFA | Costing is per unit. | Electrical | Battery Charger
641 | Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit. | Electrical | Battery Charger
642 | Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 2 | PFA | Costing is per unit. | Electrical | Battery Charger
643 | Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 4 | PFA | Costing is per unit. | Electrical | Battery Charger
644 | Diesel generator - Capacity: 100 to <350 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 4 | PFA | Costing is per unit and is based upon 250 kVa. | Electrical | Diesel generator
645 | Diesel generator - Capacity: 350 to <750 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 4 | PFA | Costing is per unit and is based upon 500 kVa. | Electrical | Diesel generator
646 | Diesel generator - Capacity: 750 to 1200 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 4 | PFA | Costing is per unit and is based upon 1000 kVa. | Electrical | Diesel generator
647 | Diesel generator - Capacity: 1200 to 2000 kVa - Unanchored equipment that is not vibration isolated - Equipment fragility only | 4 | PFA | Costing is per unit and is based upon 1500 kVa. | Electrical | Diesel generator
648 | Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 250 kVa. | Electrical | Diesel generator
649 | Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 4 | PFA | Costing is per unit and is based upon 250 kVa. | Electrical | Diesel generator
650 | Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 5 | PFA | Costing is per unit and is based upon 250 kVa. | Electrical | Diesel generator
651 | Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 500 kVa. | Electrical | Diesel generator
652 | Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 4 | PFA | Costing is per unit and is based upon 500 kVa. | Electrical | Diesel generator
653 | Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 5 | PFA | Costing is per unit and is based upon 500 kVa. | Electrical | Diesel generator
654 | Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 1000 kVa. | Electrical | Diesel generator
655 | Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 4 | PFA | Costing is per unit and is based upon 1000 kVa. | Electrical | Diesel generator
656 | Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 5 | PFA | Costing is per unit and is based upon 1000 kVa. | Electrical | Diesel generator
657 | Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 1500 kVa. | Electrical | Diesel generator
658 | Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 4 | PFA | Costing is per unit and is based upon 1500 kVa. | Electrical | Diesel generator
659 | Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 5 | PFA | Costing is per unit and is based upon 1500 kVa. | Electrical | Diesel generator
660 | Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 250 kVa. | Electrical | Diesel generator
661 | Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 4 | PFA | Costing is per unit and is based upon 250 kVa. | Electrical | Diesel generator
662 | Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 5 | PFA | Costing is per unit and is based upon 250 kVa. | Electrical | Diesel generator
663 | Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 500 kVa. | Electrical | Diesel generator
664 | Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 4 | PFA | Costing is per unit and is based upon 500 kVa. | Electrical | Diesel generator
665 | Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 5 | PFA | Costing is per unit and is based upon 500 kVa. | Electrical | Diesel generator
666 | Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 1000 kVa. | Electrical | Diesel generator
667 | Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 4 | PFA | Costing is per unit and is based upon 1000 kVa. | Electrical | Diesel generator
668 | Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 5 | PFA | Costing is per unit and is based upon 1000 kVa. | Electrical | Diesel generator
669 | Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 2 | PFA | Costing is per unit and is based upon 1500 kVa. | Electrical | Diesel generator
670 | Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 4 | PFA | Costing is per unit and is based upon 1500 kVa. | Electrical | Diesel generator
671 | Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 5 | PFA | Costing is per unit and is based upon 1500 kVa. | Electrical | Diesel generator
672 | Modular office work stations. | 1 | PFA | Unanchored and installed per manufacturer's recommendations on a carpeted floor. | Furniture | Office Work Stations
673 | Unsecured fragile objects on shelves, unknown restraint | 1 | PFA | Costing to be furnished by user. Consequence data assumes 16 SF of damage area. | Furniture | Fragile Objects
674 | Fragile contents secured by museum putty, Velcro or other weak but sticky stuff | 1 | PFA | Costing to be furnished by user. Consequence data assumes 16 SF of damage area. | Furniture | Fragile Contents
675 | Fragile contents on shelves in storage cabinets with latches | 1 | PFA | Costing to be furnished by user. Consequence data assumes 16 SF of damage area. | Furniture | Fragile Contents
676 | Unsecured fragile objects on shelves, low friction surface | 1 | PFA | Costing to be furnished by user. Consequence data assumes 16 SF of damage area. | Furniture | Fragile Objects
677 | Home entertainment equipment, unknown installation | 1 | PFA | Costing to be furnished by user. Consequence data assumes 16 SF of damage area. | Furniture | Entertainment Equipment
678 | Electronic equipment on wall mount brackets | 1 | PFA | Costing to be furnished by user. Consequence data assumes 16 SF of damage area. | Furniture | Electronic Equipment
679 | Desktop electronics including computers, monitors, stereos, etc on a slip resistant surface | 1 | PFA | Costing to be furnished by user. Consequence data assumes 16 SF of damage area. | Furniture | Desktop Electronics
680 | Desktop electronics including computers, monitors, stereos, etc, smooth surface | 1 | PFA | Costing to be furnished by user. Consequence data assumes 16 SF of damage area. | Furniture | Desktop Electronics
681 | Bookcase, 2 shelves, unanchored laterally | 1 | PFV | Standard bookcase, unanchored laterally. Bookcase is 12-5/8" deep x 29" tall | Furniture | Bookcase
682 | Bookcase, 2 shelves, anchored laterally | 1 | PFA | Standard bookcase, anchored laterally. Bookcase is 12-5/8" deep x 29" tall. | Furniture | Bookcase
683 | Bookcase, 3 shelves, unanchored laterally | 1 | PFV | Standard bookcase, unanchored laterally. Bookcase is 12-5/8" deep x 41" tall | Furniture | Bookcase
684 | Bookcase, 3 shelves, anchored laterally | 1 | PFA | Standard bookcase, anchored laterally. Bookcase is 12-5/8" deep x 41" tall. | Furniture | Bookcase
685 | Bookcase, 4 shelves, unanchored laterally | 1 | PFV | Standard bookcase, unanchored laterally. Bookcase is 12-5/8" deep x 56" tall | Furniture | Bookcase
686 | Bookcase, 4 shelves, anchored laterally | 1 | PFA | Standard bookcase, anchored laterally. Bookcase is 12-5/8" deep x 56" tall. | Furniture | Bookcase
687 | Bookcase, 5 shelves, unanchored laterally | 1 | PFV | Standard bookcase, unanchored laterally. Bookcase is 12-5/8" deep x 71" tall | Furniture | Bookcase
688 | Bookcase, 5 shelves, anchored laterally | 1 | PFA | Standard bookcase, anchored laterally. Bookcase is 12-5/8" deep x 71" tall. | Furniture | Bookcase
689 | Bookcase, 6 shelves, unanchored laterally | 1 | PFV | Standard bookcase, unanchored laterally. Bookcase is 12-5/8" deep x 81-1/4" tall | Furniture | Bookcase
690 | Bookcase, 6 shelves, anchored laterally | 1 | PFA | Standard bookcase, anchored laterally. Bookcase is 12-5/8" deep x 81-1/4" tall. | Furniture | Bookcase
691 | Vertical Filing Cabinet, 2 drawer, unanchored laterally | 1 | PFV | Filing cabinet, unanchored laterally. Cabinet has 2 drawers and is 15" deep x 24" tall | Furniture | Filing Cabinet
692 | Vertical Filing Cabinet, 2 drawer, anchored laterally | 1 | PFV | Filing cabinet, anchored laterally. Cabinet has 2 drawers and is 15" deep x 24" tall | Furniture | Filing Cabinet
693 | Vertical Filing Cabinet, 4 drawer, unanchored laterally | 1 | PFV | Filing cabinet, unanchored laterally. Cabinet has 4 drawers and is 15" deep x 52" tall | Furniture | Filing Cabinet
694 | Vertical Filing Cabinet, 4 drawer, anchored laterally | 1 | PFV | Filing cabinet, anchored laterally. Cabinet has 4 drawers and is 15" deep x 52" tall | Furniture | Filing Cabinet
695 | Lateral Filing Cabinet, 2 drawer, unanchored laterally | 1 | PFV | Filing cabinet, unanchored laterally. Cabinet has 4 drawers and is 18.6" deep x 52.5" tall | Furniture | Filing Cabinet
696 | Lateral Filing Cabinet, 2 drawer, anchored laterally | 1 | PFA | Filing cabinet, anchored laterally. Cabinet has 4 drawers and is 18.6" deep x 52.5" tall | Furniture | Filing Cabinet
697 | Lateral Filing Cabinet, 4 drawer, unanchored laterally | 1 | PFV | Filing cabinet, unanchored laterally. Cabinet has 5 drawers and is 18.6" deep x 67.75" tall | Furniture | Filing Cabinet
698 | Lateral Filing Cabinet, 4 drawer, anchored laterally | 1 | PFA | Filing cabinet, anchored laterally. Cabinet has 5 drawers and is 18.6" deep x 67.75" tall | Furniture | Filing Cabinet
699 | Storage racks designed and installed before 2007, big box retail (12' to 15' tall) | 2 | PFA | Standard pallet back to back storage rack. Three to five levels tall with total height from 15 to 20 ft. Costing assumes one single side access rack. Costing of rack and restocking based upon 50 LF of rack. Costing of rack contents to be furnished by user. | Furniture | Storage Racks
700 | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | 2 | PFA | Potable water. Costing based upon 1000 ft segments. | Plumbing | Water Piping
701 | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | 2 | PFA | Potable water. Costing based upon 1000 ft segments. | Plumbing | Water Piping
702 | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY | 2 | PFA | Potable water. Costing based upon 1000 ft segments. | Plumbing | Water Piping
703 | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | 2 | PFA | Potable water. Costing based upon 1000 ft segments. | Plumbing | Water Piping
704 | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY | 2 | PFA | Potable water. Costing based upon 1000 ft segments. | Plumbing | Water Piping
705 | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY | 1 | PFA | Potable water. Costing based upon 1000 ft segments. | Plumbing | Water Piping
706 | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 2 | PFA | Potable water. Costing based upon 1000 ft segments. | Plumbing | Water Piping
707 | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 1 | PFA | Potable water. Costing based upon 1000 ft segments. | Plumbing | Water Piping
708 | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC A or B, PIPING FRAGILITY | 2 | PFA | Potable water. Costing based upon 1000 ft segments. | Plumbing | Water Piping
709 | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC C, PIPING FRAGILITY | 2 | PFA | Potable water. Costing based upon 1000 ft segments. | Plumbing | Water Piping
710 | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F, PIPING FRAGILITY | 2 | PFA | Potable water. Costing based upon 1000 ft segments. | Plumbing | Water Piping
711 | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F, BRACING FRAGILITY | 2 | PFA | Potable water. Costing based upon 1000 ft segments. | Plumbing | Water Piping
712 | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F (OSPHD or sim), PIPING FRAGILITY | 2 | PFA | Potable water. Costing based upon 1000 ft segments. | Plumbing | Water Piping
713 | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F (OSPHD or sim), BRACING FRAGILITY | 2 | PFA | Potable water. Costing based upon 1000 ft segments. | Plumbing | Water Piping
714 | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | 2 | PFA | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
715 | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | 2 | PFA | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
716 | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY | 2 | PFA | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
717 | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | 2 | PFA | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
718 | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY | 2 | PFA | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
719 | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY | 1 | PFA | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
720 | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 2 | PFA | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
721 | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 1 | PFA | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
722 | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY | 2 | PFA | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
723 | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC C, PIPING FRAGILITY | 2 | PFA | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
724 | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, PIPING FRAGILITY | 2 | PFA | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
725 | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, BRACING FRAGILITY | 2 | PFA | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
726 | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 2 | PFA | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
727 | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 2 | PFA | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
728 | Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC A,B, BRACING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe | Plumbing | Sanitary Piping
729 | Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC C, BRACING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe | Plumbing | Sanitary Piping
730 | Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC D,E,F, BRACING FRAGILITY | 1 | PFA | Costing based upon 1000 ft segments of pipe | Plumbing | Sanitary Piping
731 | Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC D,E,F (OSHPD or sim), BRACING FRAGILITY | 1 | PFA | Costing based upon 1000 ft segments of pipe | Plumbing | Sanitary Piping
732 | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC A,B, PIPING FRAGILITY | 1 | PFA | Costing based upon 1000 ft segments of pipe | Plumbing | Sanitary Piping
733 | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC A,B, BRACING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe | Plumbing | Sanitary Piping
734 | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC C, PIPING FRAGILITY | 1 | PFA | Costing based upon 1000 ft segments of pipe | Plumbing | Sanitary Piping
735 | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC C, BRACING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe | Plumbing | Sanitary Piping
736 | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F, PIPING FRAGILITY | 1 | PFA | Costing based upon 1000 ft segments of pipe | Plumbing | Sanitary Piping
737 | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F, BRACING FRAGILITY | 1 | PFA | Costing based upon 1000 ft segments of pipe | Plumbing | Sanitary Piping
738 | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F (OSHPD or sim), PIPING FRAGILITY | 1 | PFA | Costing based upon 1000 ft segments of pipe | Plumbing | Sanitary Piping
739 | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F (OSHPD or sim), BRACING FRAGILITY | 1 | PFA | Costing based upon 1000 ft segments of pipe | Plumbing | Sanitary Piping
740 | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
741 | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
742 | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
743 | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
744 | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
745 | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY | 1 | PFA | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
746 | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
747 | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 1 | PFA | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Water Piping
748 | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Plumbing | Water Piping
749 | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, BRACING FRAGILITY | 1 | PFA | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Plumbing | Water Piping
750 | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC C, PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Plumbing | Water Piping
751 | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Plumbing | Water Piping
752 | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, BRACING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Plumbing | Water Piping
753 | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Plumbing | Water Piping
754 | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Plumbing | Water Piping
755 | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Steam Piping
756 | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Steam Piping
757 | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Steam Piping
758 | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Steam Piping
759 | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Steam Piping
760 | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY | 1 | PFA | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Steam Piping
761 | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Steam Piping
762 | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 1 | PFA | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Plumbing | Steam Piping
763 | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Plumbing | Steam Piping
764 | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC C, PIPING FRAGILITY | 2 | PFA | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Plumbing | Steam Piping
765 | Wide-Flange Steel Column - SYM-based Univariate Fragility | 5 | COL ROT | Cost is based on 1 unit | Superstructure | WF Column
766 | Wide-Flange Steel Column - CPS-based Univariate Fragility | 5 | COL ROT | Cost is based on 1 unit | Superstructure | WF Column
767 | Drywall partition, 5/8-in, one side, on metal stud | 2 | SDR | Costing is based on an area of 64 square foot | Interiors | Drywall Partition
768 | Drywall finish, 5/8-in, one side, on metal stud | 2 | SDR | Costing is based on an area of 64 square foot | Interiors | Drywall Finish
769 | Exterior glazing | 2 | SDR | Cost is based on 1 unit | Exterior Enclosure | Exterior Glazing
770 | Automatic sprinklers | 1 | PFA | Cost is based on a length of 12 feet | Fire Protection | Sprinklers
771 | Corrugated slab (90mm steel; 100mm overlay) | 3 | SDR | Costing is based on a slab area of 10.764 square feet | Interiors | Corrugated Slab